## DATABASE
key | Item | Building: | - | Baseline | Baseline2 | Baseline3 | Baseline4 | Proposed
Annual Building Utility Performance Summary Total Site Energy Total Energy [kWh] | Annual Building Utility Performance Summary | Total Site Energy | Total Energy *[MWh] | 958.5199 | 938.8632 | 957.3788 | 933.1115 | 778.6415
Annual Building Utility Performance Summary Total Site Energy Energy Per Total Building Area [kWh/m2] | Annual Building Utility Performance Summary | Total Site Energy | Energy Per Total Building Area [kWh/m2] | 155.56 | 152.37 | 155.37 | 151.43 | 126.36
Annual Building Utility Performance Summary Total Site Energy Energy Per Conditioned Building Area [kWh/m2] | Annual Building Utility Performance Summary | Total Site Energy | Energy Per Conditioned Building Area [kWh/m2] | 178.15 | 174.5 | 177.94 | 173.43 | 146.93
Annual Building Utility Performance Summary Net Site Energy Total Energy [kWh] | Annual Building Utility Performance Summary | Net Site Energy | Total Energy *[MWh] | 958.5199 | 938.8632 | 957.3788 | 933.1115 | 778.6415
Annual Building Utility Performance Summary Net Site Energy Energy Per Total Building Area [kWh/m2] | Annual Building Utility Performance Summary | Net Site Energy | Energy Per Total Building Area [kWh/m2] | 155.56 | 152.37 | 155.37 | 151.43 | 126.36
Annual Building Utility Performance Summary Net Site Energy Energy Per Conditioned Building Area [kWh/m2] | Annual Building Utility Performance Summary | Net Site Energy | Energy Per Conditioned Building Area [kWh/m2] | 178.15 | 174.5 | 177.94 | 173.43 | 146.93
Annual Building Utility Performance Summary Total Source Energy Total Energy [kWh] | Annual Building Utility Performance Summary | Total Source Energy | Total Energy *[MWh] | 2463.3506 | 2421.6166 | 2461.7676 | 2410.8657 | 2465.9575
Annual Building Utility Performance Summary Total Source Energy Energy Per Total Building Area [kWh/m2] | Annual Building Utility Performance Summary | Total Source Energy | Energy Per Total Building Area [kWh/m2] | 399.77 | 393 | 399.52 | 391.26 | 400.2
Annual Building Utility Performance Summary Total Source Energy Energy Per Conditioned Building Area [kWh/m2] | Annual Building Utility Performance Summary | Total Source Energy | Energy Per Conditioned Building Area [kWh/m2] | 457.84 | 450.09 | 457.55 | 448.09 | 465.32
Annual Building Utility Performance Summary Net Source Energy Total Energy [kWh] | Annual Building Utility Performance Summary | Net Source Energy | Total Energy *[MWh] | 2463.3506 | 2421.6166 | 2461.7676 | 2410.8657 | 2465.9575
Annual Building Utility Performance Summary Net Source Energy Energy Per Total Building Area [kWh/m2] | Annual Building Utility Performance Summary | Net Source Energy | Energy Per Total Building Area [kWh/m2] | 399.77 | 393 | 399.52 | 391.26 | 400.2
Annual Building Utility Performance Summary Net Source Energy Energy Per Conditioned Building Area [kWh/m2] | Annual Building Utility Performance Summary | Net Source Energy | Energy Per Conditioned Building Area [kWh/m2] | 457.84 | 450.09 | 457.55 | 448.09 | 465.32
Input Verification and Results Summary Program Version and Build Value | Input Verification and Results Summary | Program Version and Build | Value | EnergyPlus-Windows-64 8.1.0.008, YMD=2014.03.02 13:57 | EnergyPlus-Windows-64 8.1.0.008, YMD=2014.03.02 13:57 | EnergyPlus-Windows-64 8.1.0.008, YMD=2014.03.02 13:57 | EnergyPlus-Windows-64 8.1.0.008, YMD=2014.03.02 13:57 | EnergyPlus-Windows-64 8.1.0.008, YMD=2014.03.02 13:57
Input Verification and Results Summary RunPeriod Value | Input Verification and Results Summary | RunPeriod | Value | UNTITLED | UNTITLED | UNTITLED | UNTITLED | UNTITLED
Input Verification and Results Summary Weather File Value | Input Verification and Results Summary | Weather File | Value | BRATISLAVA - SVK IWEC Data WMO#=118160 | BRATISLAVA - SVK IWEC Data WMO#=118160 | BRATISLAVA - SVK IWEC Data WMO#=118160 | BRATISLAVA - SVK IWEC Data WMO#=118160 | BRATISLAVA - SVK IWEC Data WMO#=118160
Input Verification and Results Summary Latitude [deg] Value | Input Verification and Results Summary | Latitude [deg] | Value | 48.2 | 48.2 | 48.2 | 48.2 | 48.2
Input Verification and Results Summary Longitude [deg] Value | Input Verification and Results Summary | Longitude [deg] | Value | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
Input Verification and Results Summary Elevation [m] Value | Input Verification and Results Summary | Elevation [m] | Value | 130 | 130 | 130 | 130 | 130
Input Verification and Results Summary Time Zone Value | Input Verification and Results Summary | Time Zone | Value | 1 | 1 | 1 | 1 | 1
Input Verification and Results Summary North Axis Angle [deg] Value | Input Verification and Results Summary | North Axis Angle [deg] | Value | 0 | 0 | 0 | 0 | 0
Input Verification and Results Summary Rotation for Appendix G [deg] Value | Input Verification and Results Summary | Rotation for Appendix G [deg] | Value | 0 | 90 | 180 | 270 | 0
Input Verification and Results Summary Hours Simulated [hrs] Value | Input Verification and Results Summary | Hours Simulated [hrs] | Value | 8760 | 8760 | 8760 | 8760 | 8760
LEED Summary Interior Lighting Electric Energy Use [GJ] | LEED Summary | Interior Lighting | Electric Energy Use **[MWh] | 194.9232 | 194.9232 | 194.9232 | 194.9232 | 161.9435
LEED Summary Interior Lighting Electric Demand [W] | LEED Summary | Interior Lighting | Electric Demand [W] | 61942.65 | 61942.65 | 61942.65 | 61942.65 | 51093.14
LEED Summary Interior Lighting Natural Gas Energy Use [GJ] | LEED Summary | Interior Lighting | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting Natural Gas Demand [W] | LEED Summary | Interior Lighting | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting Additional Energy Use [GJ] | LEED Summary | Interior Lighting | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting Additional Demand [W] | LEED Summary | Interior Lighting | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Exterior Lighting Electric Energy Use [GJ] | LEED Summary | Exterior Lighting | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Exterior Lighting Electric Demand [W] | LEED Summary | Exterior Lighting | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Exterior Lighting Natural Gas Energy Use [GJ] | LEED Summary | Exterior Lighting | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Exterior Lighting Natural Gas Demand [W] | LEED Summary | Exterior Lighting | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Exterior Lighting Additional Energy Use [GJ] | LEED Summary | Exterior Lighting | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Exterior Lighting Additional Demand [W] | LEED Summary | Exterior Lighting | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Space Heating Electric Energy Use [GJ] | LEED Summary | Space Heating | Electric Energy Use **[MWh] | 0.016662 | 0.016662 | 0.016662 | 0.016662 | 17.9727
LEED Summary Space Heating Electric Demand [W] | LEED Summary | Space Heating | Electric Demand [W] | 0 | 0 | 0 | 0 | 16886.3
LEED Summary Space Heating Natural Gas Energy Use [GJ] | LEED Summary | Space Heating | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Space Heating Natural Gas Demand [W] | LEED Summary | Space Heating | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Space Heating Additional Energy Use [GJ] | LEED Summary | Space Heating | Additional Energy Use **[MWh] | 264.0149 | 254.5482 | 263.0791 | 251.1047 | 0
LEED Summary Space Heating Additional Demand [W] | LEED Summary | Space Heating | Additional Demand [W] | 164496.44 | 162367.31 | 164052.71 | 161573.11 | 0
LEED Summary Space Cooling Electric Energy Use [GJ] | LEED Summary | Space Cooling | Electric Energy Use **[MWh] | 192.0879 | 184.5844 | 191.9101 | 183.0765 | 65.3206
LEED Summary Space Cooling Electric Demand [W] | LEED Summary | Space Cooling | Electric Demand [W] | 58756.7 | 57004 | 58728.36 | 56955.46 | 14051.5
LEED Summary Space Cooling Natural Gas Energy Use [GJ] | LEED Summary | Space Cooling | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Space Cooling Natural Gas Demand [W] | LEED Summary | Space Cooling | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Space Cooling Additional Energy Use [GJ] | LEED Summary | Space Cooling | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Space Cooling Additional Demand [W] | LEED Summary | Space Cooling | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Pumps Electric Energy Use [GJ] | LEED Summary | Pumps | Electric Energy Use **[MWh] | 10.261 | 9.9472 | 10.2693 | 9.9111 | 19.3001
LEED Summary Pumps Electric Demand [W] | LEED Summary | Pumps | Electric Demand [W] | 1113.47 | 1076.72 | 1112.08 | 1073.01 | 3817.14
LEED Summary Pumps Natural Gas Energy Use [GJ] | LEED Summary | Pumps | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Pumps Natural Gas Demand [W] | LEED Summary | Pumps | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Pumps Additional Energy Use [GJ] | LEED Summary | Pumps | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Pumps Additional Demand [W] | LEED Summary | Pumps | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Heat Rejection Electric Energy Use [GJ] | LEED Summary | Heat Rejection | Electric Energy Use **[MWh] | 24.321 | 23.2129 | 24.3154 | 22.9297 | 0
LEED Summary Heat Rejection Electric Demand [W] | LEED Summary | Heat Rejection | Electric Demand [W] | 5255.95 | 5082.45 | 5249.39 | 5064.93 | 0
LEED Summary Heat Rejection Natural Gas Energy Use [GJ] | LEED Summary | Heat Rejection | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Heat Rejection Natural Gas Demand [W] | LEED Summary | Heat Rejection | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Heat Rejection Additional Energy Use [GJ] | LEED Summary | Heat Rejection | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Heat Rejection Additional Demand [W] | LEED Summary | Heat Rejection | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Interior Electric Energy Use [GJ] | LEED Summary | Fans-Interior | Electric Energy Use **[MWh] | 53.6128 | 52.352 | 53.585 | 51.8771 | 294.8757
LEED Summary Fans-Interior Electric Demand [W] | LEED Summary | Fans-Interior | Electric Demand [W] | 32836.64 | 31489.1 | 32857.23 | 31489.45 | 33670.9
LEED Summary Fans-Interior Natural Gas Energy Use [GJ] | LEED Summary | Fans-Interior | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Interior Natural Gas Demand [W] | LEED Summary | Fans-Interior | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Interior Additional Energy Use [GJ] | LEED Summary | Fans-Interior | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Interior Additional Demand [W] | LEED Summary | Fans-Interior | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Parking Garage Electric Energy Use [GJ] | LEED Summary | Fans-Parking Garage | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Parking Garage Electric Demand [W] | LEED Summary | Fans-Parking Garage | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Parking Garage Natural Gas Energy Use [GJ] | LEED Summary | Fans-Parking Garage | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Parking Garage Natural Gas Demand [W] | LEED Summary | Fans-Parking Garage | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Parking Garage Additional Energy Use [GJ] | LEED Summary | Fans-Parking Garage | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Fans-Parking Garage Additional Demand [W] | LEED Summary | Fans-Parking Garage | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Service Water Heating Electric Energy Use [GJ] | LEED Summary | Service Water Heating | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Service Water Heating Electric Demand [W] | LEED Summary | Service Water Heating | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Service Water Heating Natural Gas Energy Use [GJ] | LEED Summary | Service Water Heating | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Service Water Heating Natural Gas Demand [W] | LEED Summary | Service Water Heating | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Service Water Heating Additional Energy Use [GJ] | LEED Summary | Service Water Heating | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Service Water Heating Additional Demand [W] | LEED Summary | Service Water Heating | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Receptacle Equipment Electric Energy Use [GJ] | LEED Summary | Receptacle Equipment | Electric Energy Use **[MWh] | 204.3206 | 204.3206 | 204.3206 | 204.3206 | 204.3206
LEED Summary Receptacle Equipment Electric Demand [W] | LEED Summary | Receptacle Equipment | Electric Demand [W] | 54091.96 | 54091.96 | 54091.96 | 54091.96 | 53666.89
LEED Summary Receptacle Equipment Natural Gas Energy Use [GJ] | LEED Summary | Receptacle Equipment | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Receptacle Equipment Natural Gas Demand [W] | LEED Summary | Receptacle Equipment | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Receptacle Equipment Additional Energy Use [GJ] | LEED Summary | Receptacle Equipment | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Receptacle Equipment Additional Demand [W] | LEED Summary | Receptacle Equipment | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting (process) Electric Energy Use [GJ] | LEED Summary | Interior Lighting (process) | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting (process) Electric Demand [W] | LEED Summary | Interior Lighting (process) | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting (process) Natural Gas Energy Use [GJ] | LEED Summary | Interior Lighting (process) | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting (process) Natural Gas Demand [W] | LEED Summary | Interior Lighting (process) | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting (process) Additional Energy Use [GJ] | LEED Summary | Interior Lighting (process) | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Interior Lighting (process) Additional Demand [W] | LEED Summary | Interior Lighting (process) | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Refrigeration Equipment Electric Energy Use [GJ] | LEED Summary | Refrigeration Equipment | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Refrigeration Equipment Electric Demand [W] | LEED Summary | Refrigeration Equipment | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Refrigeration Equipment Natural Gas Energy Use [GJ] | LEED Summary | Refrigeration Equipment | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Refrigeration Equipment Natural Gas Demand [W] | LEED Summary | Refrigeration Equipment | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Refrigeration Equipment Additional Energy Use [GJ] | LEED Summary | Refrigeration Equipment | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Refrigeration Equipment Additional Demand [W] | LEED Summary | Refrigeration Equipment | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Cooking Electric Energy Use [GJ] | LEED Summary | Cooking | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Cooking Electric Demand [W] | LEED Summary | Cooking | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Cooking Natural Gas Energy Use [GJ] | LEED Summary | Cooking | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Cooking Natural Gas Demand [W] | LEED Summary | Cooking | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Cooking Additional Energy Use [GJ] | LEED Summary | Cooking | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Cooking Additional Demand [W] | LEED Summary | Cooking | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Industrial Process Electric Energy Use [GJ] | LEED Summary | Industrial Process | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Industrial Process Electric Demand [W] | LEED Summary | Industrial Process | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Industrial Process Natural Gas Energy Use [GJ] | LEED Summary | Industrial Process | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Industrial Process Natural Gas Demand [W] | LEED Summary | Industrial Process | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Industrial Process Additional Energy Use [GJ] | LEED Summary | Industrial Process | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Industrial Process Additional Demand [W] | LEED Summary | Industrial Process | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Elevators and Escalators Electric Energy Use [GJ] | LEED Summary | Elevators and Escalators | Electric Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Elevators and Escalators Electric Demand [W] | LEED Summary | Elevators and Escalators | Electric Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Elevators and Escalators Natural Gas Energy Use [GJ] | LEED Summary | Elevators and Escalators | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Elevators and Escalators Natural Gas Demand [W] | LEED Summary | Elevators and Escalators | Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Elevators and Escalators Additional Energy Use [GJ] | LEED Summary | Elevators and Escalators | Additional Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Elevators and Escalators Additional Demand [W] | LEED Summary | Elevators and Escalators | Additional Demand [W] | 0 | 0 | 0 | 0 | 0
LEED Summary Total Line Electric Energy Use [GJ] | LEED Summary | Total Line | Electric Energy Use **[MWh] | 694.2361 | 684.0501 | 694.0334 | 681.7452 | 778.4236
LEED Summary Total Line Electric Demand [W] | LEED Summary | Total Line | Electric Demand [W]
LEED Summary Total Line Natural Gas Energy Use [GJ] | LEED Summary | Total Line | Natural Gas Energy Use **[MWh] | 0 | 0 | 0 | 0 | 0
LEED Summary Total Line Natural Gas Demand [W] | LEED Summary | Total Line | Natural Gas Demand [W]
LEED Summary Total Line Additional Energy Use [GJ] | LEED Summary | Total Line | Additional Energy Use **[MWh] | 264.0149 | 254.5482 | 263.0791 | 251.1047 | 0
LEED Summary Total Line Additional Demand [W] | LEED Summary | Total Line | Additional Demand [W]
Annual Building Utility Performance Summary Total Building Area Area [m2] | Annual Building Utility Performance Summary | Total Building Area | Area [m2] | 6161.86 | 6161.86 | 6161.86 | 6161.86 | 6161.86
Annual Building Utility Performance Summary Net Conditioned Building Area Area [m2] | Annual Building Utility Performance Summary | Net Conditioned Building Area | Area [m2] | 5380.34 | 5380.34 | 5380.34 | 5380.34 | 5299.49
Annual Building Utility Performance Summary Unconditioned Building Area Area [m2] | Annual Building Utility Performance Summary | Unconditioned Building Area | Area [m2] | 781.52 | 781.52 | 781.52 | 781.52 | 862.37
Annual Building Utility Performance Summary Heating Electricity [kWh] | Annual Building Utility Performance Summary | Heating | Electricity *[MWh] | 0.01693 | 0.01624 | 0.01686 | 0.01602 | 17.9783
Annual Building Utility Performance Summary Heating Natural Gas [kWh] | Annual Building Utility Performance Summary | Heating | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heating Additional Fuel [kWh] | Annual Building Utility Performance Summary | Heating | Additional Fuel *[MWh] | 264.0895 | 254.6207 | 263.1523 | 251.1761 | 0
Annual Building Utility Performance Summary Heating District Cooling [kWh] | Annual Building Utility Performance Summary | Heating | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heating District Heating [kWh] | Annual Building Utility Performance Summary | Heating | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heating Water [m3] | Annual Building Utility Performance Summary | Heating | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Cooling Electricity [kWh] | Annual Building Utility Performance Summary | Cooling | Electricity *[MWh] | 192.1412 | 184.6373 | 191.9641 | 183.1285 | 65.3388
Annual Building Utility Performance Summary Cooling Natural Gas [kWh] | Annual Building Utility Performance Summary | Cooling | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Cooling Additional Fuel [kWh] | Annual Building Utility Performance Summary | Cooling | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Cooling District Cooling [kWh] | Annual Building Utility Performance Summary | Cooling | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Cooling District Heating [kWh] | Annual Building Utility Performance Summary | Cooling | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Cooling Water [m3] | Annual Building Utility Performance Summary | Cooling | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Lighting Electricity [kWh] | Annual Building Utility Performance Summary | Interior Lighting | Electricity *[MWh] | 194.9788 | 194.9788 | 194.9788 | 194.9788 | 161.9893
Annual Building Utility Performance Summary Interior Lighting Natural Gas [kWh] | Annual Building Utility Performance Summary | Interior Lighting | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Lighting Additional Fuel [kWh] | Annual Building Utility Performance Summary | Interior Lighting | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Lighting District Cooling [kWh] | Annual Building Utility Performance Summary | Interior Lighting | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Lighting District Heating [kWh] | Annual Building Utility Performance Summary | Interior Lighting | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Lighting Water [m3] | Annual Building Utility Performance Summary | Interior Lighting | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Lighting Electricity [kWh] | Annual Building Utility Performance Summary | Exterior Lighting | Electricity *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Lighting Natural Gas [kWh] | Annual Building Utility Performance Summary | Exterior Lighting | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Lighting Additional Fuel [kWh] | Annual Building Utility Performance Summary | Exterior Lighting | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Lighting District Cooling [kWh] | Annual Building Utility Performance Summary | Exterior Lighting | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Lighting District Heating [kWh] | Annual Building Utility Performance Summary | Exterior Lighting | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Lighting Water [m3] | Annual Building Utility Performance Summary | Exterior Lighting | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Equipment Electricity [kWh] | Annual Building Utility Performance Summary | Interior Equipment | Electricity *[MWh] | 204.3781 | 204.3781 | 204.3781 | 204.3781 | 204.3781
Annual Building Utility Performance Summary Interior Equipment Natural Gas [kWh] | Annual Building Utility Performance Summary | Interior Equipment | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Equipment Additional Fuel [kWh] | Annual Building Utility Performance Summary | Interior Equipment | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Equipment District Cooling [kWh] | Annual Building Utility Performance Summary | Interior Equipment | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Equipment District Heating [kWh] | Annual Building Utility Performance Summary | Interior Equipment | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Interior Equipment Water [m3] | Annual Building Utility Performance Summary | Interior Equipment | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Equipment Electricity [kWh] | Annual Building Utility Performance Summary | Exterior Equipment | Electricity *[MWh] | 14.6952 | 14.6952 | 14.6952 | 14.6952 | 14.6952
Annual Building Utility Performance Summary Exterior Equipment Natural Gas [kWh] | Annual Building Utility Performance Summary | Exterior Equipment | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Equipment Additional Fuel [kWh] | Annual Building Utility Performance Summary | Exterior Equipment | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Equipment District Cooling [kWh] | Annual Building Utility Performance Summary | Exterior Equipment | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Equipment District Heating [kWh] | Annual Building Utility Performance Summary | Exterior Equipment | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Exterior Equipment Water [m3] | Annual Building Utility Performance Summary | Exterior Equipment | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Fans Electricity [kWh] | Annual Building Utility Performance Summary | Fans | Electricity *[MWh] | 53.6285 | 52.3676 | 53.6009 | 51.8903 | 294.957
Annual Building Utility Performance Summary Fans Natural Gas [kWh] | Annual Building Utility Performance Summary | Fans | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Fans Additional Fuel [kWh] | Annual Building Utility Performance Summary | Fans | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Fans District Cooling [kWh] | Annual Building Utility Performance Summary | Fans | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Fans District Heating [kWh] | Annual Building Utility Performance Summary | Fans | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Fans Water [m3] | Annual Building Utility Performance Summary | Fans | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Pumps Electricity [kWh] | Annual Building Utility Performance Summary | Pumps | Electricity *[MWh] | 10.2626 | 9.9503 | 10.2715 | 9.9137 | 19.3047
Annual Building Utility Performance Summary Pumps Natural Gas [kWh] | Annual Building Utility Performance Summary | Pumps | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Pumps Additional Fuel [kWh] | Annual Building Utility Performance Summary | Pumps | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Pumps District Cooling [kWh] | Annual Building Utility Performance Summary | Pumps | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Pumps District Heating [kWh] | Annual Building Utility Performance Summary | Pumps | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Pumps Water [m3] | Annual Building Utility Performance Summary | Pumps | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Rejection Electricity [kWh] | Annual Building Utility Performance Summary | Heat Rejection | Electricity *[MWh] | 24.3291 | 23.2189 | 24.3211 | 22.9349 | 0
Annual Building Utility Performance Summary Heat Rejection Natural Gas [kWh] | Annual Building Utility Performance Summary | Heat Rejection | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Rejection Additional Fuel [kWh] | Annual Building Utility Performance Summary | Heat Rejection | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Rejection District Cooling [kWh] | Annual Building Utility Performance Summary | Heat Rejection | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Rejection District Heating [kWh] | Annual Building Utility Performance Summary | Heat Rejection | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Rejection Water [m3] | Annual Building Utility Performance Summary | Heat Rejection | Water [m3] | 1406.56 | 1357.82 | 1405.66 | 1347.07 | 0
Annual Building Utility Performance Summary Humidification Electricity [kWh] | Annual Building Utility Performance Summary | Humidification | Electricity *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Humidification Natural Gas [kWh] | Annual Building Utility Performance Summary | Humidification | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Humidification Additional Fuel [kWh] | Annual Building Utility Performance Summary | Humidification | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Humidification District Cooling [kWh] | Annual Building Utility Performance Summary | Humidification | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Humidification District Heating [kWh] | Annual Building Utility Performance Summary | Humidification | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Humidification Water [m3] | Annual Building Utility Performance Summary | Humidification | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Recovery Electricity [kWh] | Annual Building Utility Performance Summary | Heat Recovery | Electricity *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Recovery Natural Gas [kWh] | Annual Building Utility Performance Summary | Heat Recovery | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Recovery Additional Fuel [kWh] | Annual Building Utility Performance Summary | Heat Recovery | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Recovery District Cooling [kWh] | Annual Building Utility Performance Summary | Heat Recovery | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Recovery District Heating [kWh] | Annual Building Utility Performance Summary | Heat Recovery | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Heat Recovery Water [m3] | Annual Building Utility Performance Summary | Heat Recovery | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Water Systems Electricity [kWh] | Annual Building Utility Performance Summary | Water Systems | Electricity *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Water Systems Natural Gas [kWh] | Annual Building Utility Performance Summary | Water Systems | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Water Systems Additional Fuel [kWh] | Annual Building Utility Performance Summary | Water Systems | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Water Systems District Cooling [kWh] | Annual Building Utility Performance Summary | Water Systems | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Water Systems District Heating [kWh] | Annual Building Utility Performance Summary | Water Systems | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Water Systems Water [m3] | Annual Building Utility Performance Summary | Water Systems | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Refrigeration Electricity [kWh] | Annual Building Utility Performance Summary | Refrigeration | Electricity *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Refrigeration Natural Gas [kWh] | Annual Building Utility Performance Summary | Refrigeration | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Refrigeration Additional Fuel [kWh] | Annual Building Utility Performance Summary | Refrigeration | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Refrigeration District Cooling [kWh] | Annual Building Utility Performance Summary | Refrigeration | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Refrigeration District Heating [kWh] | Annual Building Utility Performance Summary | Refrigeration | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Refrigeration Water [m3] | Annual Building Utility Performance Summary | Refrigeration | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Generators Electricity [kWh] | Annual Building Utility Performance Summary | Generators | Electricity *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Generators Natural Gas [kWh] | Annual Building Utility Performance Summary | Generators | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Generators Additional Fuel [kWh] | Annual Building Utility Performance Summary | Generators | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Generators District Cooling [kWh] | Annual Building Utility Performance Summary | Generators | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Generators District Heating [kWh] | Annual Building Utility Performance Summary | Generators | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Generators Water [m3] | Annual Building Utility Performance Summary | Generators | Water [m3] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Electricity [kWh] | Annual Building Utility Performance Summary |  | Electricity *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Natural Gas [kWh] | Annual Building Utility Performance Summary |  | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Additional Fuel [kWh] | Annual Building Utility Performance Summary |  | Additional Fuel *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary District Cooling [kWh] | Annual Building Utility Performance Summary |  | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary District Heating [kWh] | Annual Building Utility Performance Summary |  | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Water [m3] | Annual Building Utility Performance Summary |  | Water [m3]
Annual Building Utility Performance Summary Total End Uses Electricity [kWh] | Annual Building Utility Performance Summary | Total End Uses | Electricity *[MWh] | 694.4304 | 684.2425 | 694.2265 | 681.9355 | 778.6415
Annual Building Utility Performance Summary Total End Uses Natural Gas [kWh] | Annual Building Utility Performance Summary | Total End Uses | Natural Gas *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Total End Uses Additional Fuel [kWh] | Annual Building Utility Performance Summary | Total End Uses | Additional Fuel *[MWh] | 264.0895 | 254.6207 | 263.1523 | 251.1761 | 0
Annual Building Utility Performance Summary Total End Uses District Cooling [kWh] | Annual Building Utility Performance Summary | Total End Uses | District Cooling *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Total End Uses District Heating [kWh] | Annual Building Utility Performance Summary | Total End Uses | District Heating *[MWh] | 0 | 0 | 0 | 0 | 0
Annual Building Utility Performance Summary Total End Uses Water [m3] | Annual Building Utility Performance Summary | Total End Uses | Water [m3] | 1406.56 | 1357.82 | 1405.66 | 1347.07 | 0
Annual Building Utility Performance Summary Time Setpoint Not Met During Occupied Heating Facility [Hours] | Annual Building Utility Performance Summary | Time Setpoint Not Met During Occupied Heating | Facility [Hours] | 0 | 0 | 0 | 0 | 11.75
Annual Building Utility Performance Summary Time Setpoint Not Met During Occupied Cooling Facility [Hours] | Annual Building Utility Performance Summary | Time Setpoint Not Met During Occupied Cooling | Facility [Hours] | 10.5 | 10.5 | 16.5 | 15 | 3118.25
Annual Building Utility Performance Summary Time Not Comfortable Based on Simple ASHRAE 55-2004 Facility [Hours] | Annual Building Utility Performance Summary | Time Not Comfortable Based on Simple ASHRAE 55-2004 | Facility [Hours] | 3120 | 3120 | 3120 | 3120 | 3117
Input Verification and Results Summary Gross Wall Area [m2] Total | Input Verification and Results Summary | Gross Wall Area [m2] | Total | 3361.58 | 3361.58 | 3361.58 | 3361.58 | 3361.58
Input Verification and Results Summary Gross Wall Area [m2] North (315 to 45 deg) | Input Verification and Results Summary | Gross Wall Area [m2] | North (315 to 45 deg) | 702.94 | 977.85 | 702.94 | 977.85 | 702.94
Input Verification and Results Summary Gross Wall Area [m2] East (45 to 135 deg) | Input Verification and Results Summary | Gross Wall Area [m2] | East (45 to 135 deg) | 977.85 | 702.94 | 977.85 | 702.94 | 977.85
Input Verification and Results Summary Gross Wall Area [m2] South (135 to 225 deg) | Input Verification and Results Summary | Gross Wall Area [m2] | South (135 to 225 deg) | 702.94 | 977.85 | 702.94 | 977.85 | 702.94
Input Verification and Results Summary Gross Wall Area [m2] West (225 to 315 deg) | Input Verification and Results Summary | Gross Wall Area [m2] | West (225 to 315 deg) | 977.85 | 702.94 | 977.85 | 702.94 | 977.85
Input Verification and Results Summary Above Ground Wall Area [m2] Total | Input Verification and Results Summary | Above Ground Wall Area [m2] | Total | 3361.58 | 3361.58 | 3361.58 | 3361.58 | 3361.58
Input Verification and Results Summary Above Ground Wall Area [m2] North (315 to 45 deg) | Input Verification and Results Summary | Above Ground Wall Area [m2] | North (315 to 45 deg) | 702.94 | 977.85 | 702.94 | 977.85 | 702.94
Input Verification and Results Summary Above Ground Wall Area [m2] East (45 to 135 deg) | Input Verification and Results Summary | Above Ground Wall Area [m2] | East (45 to 135 deg) | 977.85 | 702.94 | 977.85 | 702.94 | 977.85
Input Verification and Results Summary Above Ground Wall Area [m2] South (135 to 225 deg) | Input Verification and Results Summary | Above Ground Wall Area [m2] | South (135 to 225 deg) | 702.94 | 977.85 | 702.94 | 977.85 | 702.94
Input Verification and Results Summary Above Ground Wall Area [m2] West (225 to 315 deg) | Input Verification and Results Summary | Above Ground Wall Area [m2] | West (225 to 315 deg) | 977.85 | 702.94 | 977.85 | 702.94 | 977.85
Input Verification and Results Summary Window Opening Area [m2] Total | Input Verification and Results Summary | Window Opening Area [m2] | Total | 1229.93 | 1229.93 | 1229.93 | 1229.93 | 1002.62
Input Verification and Results Summary Window Opening Area [m2] North (315 to 45 deg) | Input Verification and Results Summary | Window Opening Area [m2] | North (315 to 45 deg) | 251.85 | 358.8 | 255.3 | 363.98 | 209.26
Input Verification and Results Summary Window Opening Area [m2] East (45 to 135 deg) | Input Verification and Results Summary | Window Opening Area [m2] | East (45 to 135 deg) | 363.98 | 251.85 | 358.8 | 255.3 | 292.05
Input Verification and Results Summary Window Opening Area [m2] South (135 to 225 deg) | Input Verification and Results Summary | Window Opening Area [m2] | South (135 to 225 deg) | 255.3 | 363.98 | 251.85 | 358.8 | 209.58
Input Verification and Results Summary Window Opening Area [m2] West (225 to 315 deg) | Input Verification and Results Summary | Window Opening Area [m2] | West (225 to 315 deg) | 358.8 | 255.3 | 363.98 | 251.85 | 291.73
Input Verification and Results Summary Gross Window-Wall Ratio [%] Total | Input Verification and Results Summary | Gross Window-Wall Ratio [%] | Total | 36.59 | 36.59 | 36.59 | 36.59 | 29.83
Input Verification and Results Summary Gross Window-Wall Ratio [%] North (315 to 45 deg) | Input Verification and Results Summary | Gross Window-Wall Ratio [%] | North (315 to 45 deg) | 35.83 | 36.69 | 36.32 | 37.22 | 29.77
Input Verification and Results Summary Gross Window-Wall Ratio [%] East (45 to 135 deg) | Input Verification and Results Summary | Gross Window-Wall Ratio [%] | East (45 to 135 deg) | 37.22 | 35.83 | 36.69 | 36.32 | 29.87
Input Verification and Results Summary Gross Window-Wall Ratio [%] South (135 to 225 deg) | Input Verification and Results Summary | Gross Window-Wall Ratio [%] | South (135 to 225 deg) | 36.32 | 37.22 | 35.83 | 36.69 | 29.81
Input Verification and Results Summary Gross Window-Wall Ratio [%] West (225 to 315 deg) | Input Verification and Results Summary | Gross Window-Wall Ratio [%] | West (225 to 315 deg) | 36.69 | 36.32 | 37.22 | 35.83 | 29.83
Input Verification and Results Summary Above Ground Window-Wall Ratio [%] Total | Input Verification and Results Summary | Above Ground Window-Wall Ratio [%] | Total | 36.59 | 36.59 | 36.59 | 36.59 | 29.83
Input Verification and Results Summary Above Ground Window-Wall Ratio [%] North (315 to 45 deg) | Input Verification and Results Summary | Above Ground Window-Wall Ratio [%] | North (315 to 45 deg) | 35.83 | 36.69 | 36.32 | 37.22 | 29.77
Input Verification and Results Summary Above Ground Window-Wall Ratio [%] East (45 to 135 deg) | Input Verification and Results Summary | Above Ground Window-Wall Ratio [%] | East (45 to 135 deg) | 37.22 | 35.83 | 36.69 | 36.32 | 29.87
Input Verification and Results Summary Above Ground Window-Wall Ratio [%] South (135 to 225 deg) | Input Verification and Results Summary | Above Ground Window-Wall Ratio [%] | South (135 to 225 deg) | 36.32 | 37.22 | 35.83 | 36.69 | 29.81
Input Verification and Results Summary Above Ground Window-Wall Ratio [%] West (225 to 315 deg) | Input Verification and Results Summary | Above Ground Window-Wall Ratio [%] | West (225 to 315 deg) | 36.69 | 36.32 | 37.22 | 35.83 | 29.83
Item Lighting Average LPD [W/m2] | Item | Lighting | Average LPD [W/m2] | 10.8766 | 10.8766 | 10.8766 | 10.8766 | 9.0719
Item Envelope Average External U | Item | Envelope | Average External U | 0.45448 | 0.45448 | 0.45448 | 0.45448 | 0.2095
Item Envelope Average Window U | Item | Envelope | Average Window U | 2.493 | 2.493 | 2.493 | 2.493 | 0.78
Zone Summary Total Area m2 | Zone Summary | Total Area | m2 | 6161.86 | 6161.86 | 6161.86 | 6161.86 | 6161.86
Zone Summary Conditioned Area m2 | Zone Summary | Conditioned Area | m2 | 5380.34 | 5380.34 | 5380.34 | 5380.34 | 5299.49
Zone Summary Unconditioned Area m2 | Zone Summary | Unconditioned Area | m2 | 781.52 | 781.52 | 781.52 | 781.52 | 862.37
Zone Summary Volume [m3] | Zone Summary | Volume | [m3] | 22798.88 | 22798.88 | 22798.88 | 22798.88 | 22798.88
Zone Summary Gross Wall Area [m2] | Zone Summary | Gross Wall Area | [m2] | 3361.58 | 3361.58 | 3361.58 | 3361.58 | 3361.58
Zone Summary Window Glass Area [m2] | Zone Summary | Window Glass Area | [m2] | 113.96 | 113.96 | 113.96 | 113.96 | 431.44
Zone Summary Avg Lighting LPD W/m2 | Zone Summary | Avg Lighting LPD | W/m2 | 10.5268 | 10.5268 | 10.5268 | 10.5268 | 8.6248
Zone Summary Avg Occupancy Density m2/Pers | Zone Summary | Avg Occupancy Density | m2/Pers | 8.55 | 8.55 | 8.55 | 8.55 | 8.55
Zone Summary Avg Plug load W/m2 [-] | Zone Summary | Avg Plug load | W/m2 [-] | 9.1066 | 9.1066 | 9.1066 | 9.1066 | 9.1066
Sensible summary HVAC Input Sensible Air Heating [GJ] [GJ] | Sensible summary | HVAC Input Sensible Air Heating [GJ] | **[MWh] | 109.6546 | 108.2022 | 109.4077 | 107.3283 | 74.7741
Sensible summary HVAC Input Sensible Air Cooling [GJ] [GJ] | Sensible summary | HVAC Input Sensible Air Cooling [GJ] | **[MWh] | -448.2622 | -442.1226 | -448.834 | -441.0237 | -341.5841
Sensible summary HVAC Input Heated Surface Heating [GJ] [GJ] | Sensible summary | HVAC Input Heated Surface Heating [GJ] | **[MWh] | 0 | 0 | 0 | 0 | 7.0605
Sensible summary HVAC Input Cooled Surface Cooling [GJ] [GJ] | Sensible summary | HVAC Input Cooled Surface Cooling [GJ] | **[MWh] | 0 | 0 | 0 | 0 | -345.566
Sensible summary People Sensible Heat Addition [GJ] [GJ] | Sensible summary | People Sensible Heat Addition [GJ] | **[MWh] | 112.0661 | 111.5915 | 112.0003 | 111.5799 | 43.2198
Sensible summary Lights Sensible Heat Addition [GJ] [GJ] | Sensible summary | Lights Sensible Heat Addition [GJ] | **[MWh] | 194.9243 | 194.9243 | 194.9243 | 194.9243 | 161.9438
Sensible summary Equipment Sensible Heat Addition [GJ] [GJ] | Sensible summary | Equipment Sensible Heat Addition [GJ] | **[MWh] | 204.3208 | 204.3208 | 204.3208 | 204.3208 | 204.3208
Sensible summary Window Heat Addition [GJ] [GJ] | Sensible summary | Window Heat Addition [GJ] | **[MWh] | 236.3399 | 233.739 | 237.5532 | 233.9959 | 210.937
Sensible summary Interzone Air Transfer Heat Addition [GJ] [GJ] | Sensible summary | Interzone Air Transfer Heat Addition [GJ] | **[MWh] | 0 | 0 | 0 | 0 | 0
Sensible summary Infiltration Heat Addition [GJ] [GJ] | Sensible summary | Infiltration Heat Addition [GJ] | **[MWh] | 1.3832 | 1.3843 | 1.3849 | 1.3791 | 0
Sensible summary Opaque Surface Conduction and Other Heat Addition [GJ] [GJ] | Sensible summary | Opaque Surface Conduction and Other Heat Addition [GJ] | **[MWh] | 8.9225 | 8.7473 | 8.8539 | 8.6542 | 228.6568
Sensible summary Equipment Sensible Heat Removal [GJ] [GJ] | Sensible summary | Equipment Sensible Heat Removal [GJ] | **[MWh] | 0 | 0 | 0 | 0 | 0
Sensible summary Window Heat Removal [GJ] [GJ] | Sensible summary | Window Heat Removal [GJ] | **[MWh] | -211.5352 | -212.2669 | -211.4658 | -212.4441 | -113.8006
Sensible summary Interzone Air Transfer Heat Removal [GJ] [GJ] | Sensible summary | Interzone Air Transfer Heat Removal [GJ] | **[MWh] | 0 | 0 | 0 | 0 | 0
Sensible summary Infiltration Heat Removal [GJ] [GJ] | Sensible summary | Infiltration Heat Removal [GJ] | **[MWh] | -83.3244 | -83.6016 | -83.3367 | -83.6735 | -45.8252
Sensible summary Opaque Surface Conduction and Other Heat Removal [GJ] [GJ] | Sensible summary | Opaque Surface Conduction and Other Heat Removal [GJ] | **[MWh] | -124.4899 | -124.9183 | -124.8089 | -125.0411 | -84.1453
Item Outdoor Air Summary Average outdoor air occupied [m3/s] | Item | Outdoor Air Summary | Average outdoor air occupied [m3/s] | 3.1298 | 3.1345 | 3.1327 | 3.1302 | 9.1218
Item Outdoor Air Summary Minimum outdoor air occupied [m3/s] | Item | Outdoor Air Summary | Minimum outdoor air occupied [m3/s] | 2.1517 | 2.0009 | 2.0921 | 2.0052 | 8.4477
Item Envelope Summary Average glass U-Factor [W/m2-K] | Item | Envelope Summary | Average glass U-Factor [W/m2-K] | 2.493 | 2.493 | 2.493 | 2.493 | 0.78
Item Envelope Summary Average glass SHGC | Item | Envelope Summary | Average glass SHGC | 0.426 | 0.426 | 0.426 | 0.426 | 0.474
Item Envelope Summary Average glass visible transmittance | Item | Envelope Summary | Average glass visible transmittance | 0.308 | 0.308 | 0.308 | 0.308 | 0.661
Item HVAC Sizing Summary Total Calculated Design Cooling Load [W] | Item | HVAC Sizing Summary | Total Calculated Design Cooling Load [W] | 250572.26 | 237922.36 | 249560.13 | 236323.98 | 276042.53
Item HVAC Sizing Summary Total User Design Cooling Load [W] | Item | HVAC Sizing Summary | Total User Design Cooling Load [W] | 288158.09 | 273610.72 | 286994.15 | 271772.58 | 317448.92
Item HVAC Sizing Summary Total Calculated Design Cooling Air Flow [m3/s] | Item | HVAC Sizing Summary | Total Calculated Design Cooling Air Flow [m3/s] | 18.619 | 17.676 | 18.546 | 17.557 | 22.076
Item HVAC Sizing Summary Total User Design Cooling Air Flow [m3/s] | Item | HVAC Sizing Summary | Total User Design Cooling Air Flow [m3/s] | 21.416 | 20.338 | 21.329 | 20.201 | 25.814
Item HVAC Sizing Summary Total Calculated Design Heating Load [W] | Item | HVAC Sizing Summary | Total Calculated Design Heating Load [W] | 154472.72 | 154231.68 | 154491.36 | 154239.91 | 166288.44
Item HVAC Sizing Summary Total User Design Heating Load [W] | Item | HVAC Sizing Summary | Total User Design Heating Load [W] | 193090.93 | 192789.7 | 193114.23 | 192799.85 | 207860.6
Item HVAC Sizing Summary Total Calculated Design Heating Air Flow [m3/s] | Item | HVAC Sizing Summary | Total Calculated Design Heating Air Flow [m3/s] | 11.586 | 11.567 | 11.586 | 11.568 | 4.708
Item HVAC Sizing Summary Total User Design Heating Air Flow [m3/s] | Item | HVAC Sizing Summary | Total User Design Heating Air Flow [m3/s] | 14.547 | 14.521 | 14.545 | 14.522 | 8.765

## Fuel
KEY
|  |  | AD | BL | AD | BL |  | AD |  |  | BL |  |  |  | Proposed | Baseline | Baseline2 | Baseline3 | Baseline4
|  |  | FLH | FLH | MWh | MWh |  | elec | gas | other | elec | gas | other |  | MWh | MWh | MWh | MWh | MWh
[14 empty] | Input Verification and Results Summary Rotation for Appendix G [deg] Value | 0 | 0 | 90 | 180 | 270 | 0 |  |  | 135
[14 empty] | Input Verification and Results Summary Hours Simulated [hrs] Value | 8760 | 8760 | 8760 | 8760 | 8760 | 1 |  |  | 8760
#DIV/0!
| Lighting | elec |  |  | 161.9435 | 194.9232 | 16.92% | 161.9435 | 0 | 0 | 194.9232 | 0 | 0 | LEED Summary Interior Lighting Electric Energy Use [GJ] | 161.9435 | 194.9232 | 194.9232 | 194.9232 | 194.9232 | 0 | 54092929.1329 | 44940780.364 | 194.9232
|  |  | 3169.5749 | 3146.8331 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Interior Lighting Electric Demand [W] | 51093.14 | 61942.65 | 61942.65 | 61942.65 | 61942.65 | 1 | 3169.5749 | 3146.8331 | 61942.65
| Space heating elec | elec |  |  | 17.9727 | 0.016662 | -107767% | 17.9727 | 0 | 0 | 0.016662 | 0 | 0 | LEED Summary Space Heating Electric Energy Use [GJ] | 17.9727 | 0.016662 | 0.016662 | 0.016662 | 0.016662 | 0 | 2842812427.5292 | 3.7176e+12 | 0.016662
|  |  | 1064.3388 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Space Heating Electric Demand [W] | 16886.3 | 0 | 0 | 0 | 0 | 1 | 1064.3388 | #DIV/0! | 0
| Space heating gas | gas |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Space Heating Natural Gas Energy Use [GJ] | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Space Heating Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0! | 0
| Space heating other | other |  |  | 0 | 258.1867 | 100% | 0 | 0 | 0 | 0 | 0 | 258.1867 | LEED Summary Space Heating Additional Energy Use [GJ] | 0 | 264.0149 | 254.5482 | 263.0791 | 251.1047 | 0 | #DIV/0! | 0 | 258.1867
|  |  |  | 1604.9888 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Space Heating Additional Demand [W] | 0 | 164496.44 | 162367.31 | 164052.71 | 161573.11 | 1 | #DIV/0! | 1604.9888 | 163122.3925
| Space cooling | elec |  |  | 65.3206 | 187.9147 | 65.24% | 65.3206 | 0 | 0 | 187.9147 | 0 | 0 | LEED Summary Space Cooling Electric Energy Use [GJ] | 65.3206 | 192.0879 | 184.5844 | 191.9101 | 183.0765 | 0 | 0 | 856360386.3642 | 187.9147
|  |  | 4648.6563 | 3269.2079 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Space Cooling Electric Demand [W] | 14051.5 | 58756.7 | 57004 | 58728.36 | 56955.46 | 1 | 4648.6563 | 3269.2079 | 57861.13
| Pumps | elec |  |  | 19.3001 | 10.0972 | -91.14% | 19.3001 | 0 | 0 | 10.0972 | 0 | 0 | LEED Summary Pumps Electric Energy Use [GJ] | 19.3001 | 10.261 | 9.9472 | 10.2693 | 9.9111 | 0 | #REF! | #REF! | 10.0972
|  |  | 5056.1808 | 9215.3493 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Pumps Electric Demand [W] | 3817.14 | 1113.47 | 1076.72 | 1112.08 | 1073.01 | 1 | 5056.1808 | 9215.3493 | 1093.82
| Heat rejection | elec |  |  | 0 | 23.6948 | 100% | 0 | 0 | 0 | 23.6948 | 0 | 0 | LEED Summary Heat Rejection Electric Energy Use [GJ] | 0 | 24.321 | 23.2129 | 24.3154 | 22.9297 | 0 | #REF! | #REF! | 23.6948
|  |  |  | 4627.3207 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Heat Rejection Electric Demand [W] | 0 | 5255.95 | 5082.45 | 5249.39 | 5064.93 | 1 | #DIV/0! | 4627.3207 | 5163.18
| Fans | elec |  |  | 294.8757 | 52.8567 | -457.9% | 294.8757 | 0 | 0 | 52.8567 | 0 | 0 | LEED Summary Fans-Interior Electric Energy Use [GJ] | 294.8757 | 53.6128 | 52.352 | 53.585 | 51.8771 | 0 | #REF! | #REF! | 52.8567
|  |  | 8757.5843 | 1632.7116 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Fans-Interior Electric Demand [W] | 33670.9 | 32836.64 | 31489.1 | 32857.23 | 31489.45 | 1 | 8757.5843 | 1632.7116 | 32168.105
| Parking fans | elec |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Fans-Parking Garage Electric Energy Use [GJ] | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Fans-Parking Garage Electric Demand [W] | 0 | 0 | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0! | 0
| DHW elec | elec |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Service Water Heating Electric Energy Use [GJ] | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Service Water Heating Electric Demand [W] | 0 | 0 | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0! | 0
| DHW gas | gas |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Service Water Heating Natural Gas Energy Use [GJ] | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Service Water Heating Natural Gas Demand [W] | 0 | 0 | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0! | 0
| DHW other | other |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Service Water Heating Additional Energy Use [GJ] | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Service Water Heating Additional Demand [W] | 0 | 0 | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0! | 0
| Plug load | elec |  |  | 204.3206 | 204.3206 | 0% | 204.3206 | 0 | 0 | 204.3206 | 0 | 0 | LEED Summary Receptacle Equipment Electric Energy Use [GJ] | 204.3206 | 204.3206 | 204.3206 | 204.3206 | 204.3206 | 0 | 0 | 0 | 204.3206
|  |  | 3807.1994 | 3777.2814 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Receptacle Equipment Electric Demand [W] | 53666.89 | 54091.96 | 54091.96 | 54091.96 | 54091.96 | 1 | 3807.1994 | 3777.2814 | 54091.96
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryInterior Lighting (process)Electric Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #REF! | #REF! | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryInterior Lighting (process)Electric Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryRefrigeration EquipmentElectric Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #REF! | #REF! | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryRefrigeration EquipmentElectric Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryCookingElectric Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #REF! | #REF! | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryCookingElectric Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryCookingNatural Gas Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryCookingNatural Gas Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryCookingAdditional Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryCookingAdditional Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryIndustrial ProcessElectric Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryIndustrial ProcessElectric Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryIndustrial ProcessNatural Gas Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryIndustrial ProcessNatural Gas Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
[5 empty] | #N/A | #N/A | #N/A | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryIndustrial ProcessAdditional Energy Use **[MWh] | #N/A | #N/A | #N/A | #N/A | #N/A | 0 | #N/A | #N/A | #N/A
|  |  | #N/A | #N/A |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED SummaryIndustrial ProcessAdditional Demand [W] | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
| Elevators | elec |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Elevators and Escalators Electric Energy Use [GJ] | 0 | 0 | 0 | 0 | 0 | 0 | #N/A | #N/A | 0
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 | LEED Summary Elevators and Escalators Electric Demand [W] | 0 | 0 | 0 | 0 | 0 | 1 | #DIV/0! | #DIV/0! | 0
| Exterior equipment | elec |  |  | 14.6952 | 14.6952 | 0% | 14.6952 | 0 | 0 | 14.6952 | 0 | 0 | Annual Building Utility Performance Summary Exterior Equipment Electricity [kWh] | 14.6952 | 14.6952 | 14.6952 | 14.6952 | 14.6952 | 0 | 0 | 0 | 14.6952
[8 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | #N/A | #N/A | #N/A | #N/A | #N/A | 1 | #N/A | #N/A | #N/A
| Total elec |  |  |  | 778.4236 | 688.5162 | -13.06% | 778.4285 | 0 | 0 | 688.519 | 0 | 258.1867 | LEED Summary Total Line Electric Energy Use [GJ] | 778.4236 | 694.2361 | 684.0501 | 694.0334 | 681.7452 | 0 | #REF! | #REF! | 688.5162
| Total gas |  |  |  | 0 | 0 | [7 empty] | LEED Summary Total Line Natural Gas Energy Use [GJ] | 0 | 0 | 0 | 0 | 0 | 0 | #REF! | #REF! | 0
| Total other |  |  |  | 0 | 258.1867 | 100% | [6 empty] | LEED Summary Total Line Additional Energy Use [GJ] | 0 | 264.0149 | 254.5482 | 263.0791 | 251.1047 | 0 | #REF! | #REF! | 258.1867
#DIV/0!
Calculated process load compliance
| Process loads |  |  |  | 219.0158 | 219.0158
| Total loads |  |  |  | 778.4236 | 946.7029
| Process percent |  |  |  | 28.14% | 23.13%
Calculated Fuel totals | [22 empty] | #DIV/0!
| Elec |  | MWh | OK | 778.4285 | 688.519 | -13.06%
| Gas |  | MWh | N/A | 0 | 0
| Other Fuel |  | MWh | N/A | 0 | 258.1867 | 100%
Cost totals
|  |  |  | Rate | AD | BL
[5 empty] | kUSD | kUSD
| Total elec |  | USD | 0.19 | 147.9014 | 130.8186 | -13.06%
| Total gas |  | USD | 0 | 0 | 0
| Total other |  | USD | 0.1033 | 0 | 26.6707 | 100%
[5 empty] | Cost | Cost | Savings
[5 empty] | AD kUSD | BL kUSD | kUSD
|  |  | USD |  | 147.9014 | 157.4893 | 9.5879
[6 empty] | Total | 6.088%
Specific values
|  |  | Per conditioned area |  | Per total area |  | (Benchmark) | Diff (%)
|  |  | AD | BL | AD | BL
| Heating kWh/m2 |  | 3.3914 | 47.9871 | 2.9168 | 41.9008 | 24.63 | 744.4%
| Cooling kWh/m2 |  | 12.3258 | 35.459 | 10.6008 | 30.4964 | 29.95 | 58.18%
| Ventilation kWh/m2 |  | 59.2842 | 11.7007 | 50.9872 | 10.2167
| DHW kWh/m2 |  | 0 | 0 | 0 | 0 | 0.53 | #DIV/0!
| Lighting kWh/m2 |  | 30.5583 | 36.2288 | 26.2816 | 31.6338 | 19.91 | 24.24%

## Overview
|  |  | Proposed | Baseline AVG |  | Proposed | Baseline | Baseline2 | Baseline3 | Baseline4 | Baseline
Simulation
| Rotation |  | 0 | 135 | Input Verification and Results Summary Rotation for Appendix G [deg] Value | 0 | 0 | 90 | 180 | 270 | 135
| Hours |  | 8760 | 8760 | Input Verification and Results Summary Hours Simulated [hrs] Value | 8760 | 8760 | 8760 | 8760 | 8760 | 8760
Setpoints not met | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| Not met heating |  | 11.75 | 0 | Annual Building Utility Performance Summary Time Setpoint Not Met During Occupied Heating Facility [Hours] | 11.75 | 0 | 0 | 0 | 0 | 0
| Not met cooling |  | 3118.25 | 13.125 | Annual Building Utility Performance Summary Time Setpoint Not Met During Occupied Cooling Facility [Hours] | 3118.25 | 10.5 | 10.5 | 16.5 | 15 | 13.125
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
Building envelope | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| WWR |  | 29.83 | 36.59 | Input Verification and Results Summary Above Ground Window-Wall Ratio [%] Total | 29.83 | 36.59 | 36.59 | 36.59 | 36.59 | 36.59
| Average Wall U |  | 0.2095 | 0.45448 | Item Envelope Average External U | 0.2095 | 0.45448 | 0.45448 | 0.45448 | 0.45448 | 0.45448
| Average Window U |  | 0.78 | 2.493 | Item Envelope Average Window U | 0.78 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493
| Glass SHGC |  | 0.474 | 0.426 | Item Envelope Summary Average glass SHGC | 0.474 | 0.426 | 0.426 | 0.426 | 0.426 | 0.426
| Glass vis. Trans |  | 0.661 | 0.308 | Item Envelope Summary Average glass visible transmittance | 0.661 | 0.308 | 0.308 | 0.308 | 0.308 | 0.308
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
Areas | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| Total zone area |  | 6161.86 | 6161.86 | Zone Summary Total Area m2 | 6161.86 | 6161.86 | 6161.86 | 6161.86 | 6161.86 | 6161.86
| Total cond area |  | 5299.49 | 5380.34 | Zone Summary Conditioned Area m2 | 5299.49 | 5380.34 | 5380.34 | 5380.34 | 5380.34 | 5380.34
| Total uncon area |  | 862.37 | 781.52 | Zone Summary Unconditioned Area m2 | 862.37 | 781.52 | 781.52 | 781.52 | 781.52 | 781.52
[6 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
Loads | [5 empty] | #N/A | #N/A | #N/A | #N/A | #N/A
| Avg lighting | w/m2 | 8.6248 | 10.5268 | Zone Summary Avg Lighting LPD W/m2 | 8.6248 | 10.5268 | 10.5268 | 10.5268 | 10.5268 | 10.5268
| Plug loads |  | 9.1066 | 9.1066 | Zone Summary Avg Plug load W/m2 [-] | 9.1066 | 9.1066 | 9.1066 | 9.1066 | 9.1066 | 9.1066
| Occ dens | m2/pers | 8.55 | 8.55 | Zone Summary Avg Occupancy Density m2/Pers | 8.55 | 8.55 | 8.55 | 8.55 | 8.55 | 8.55
| Occupancy |  | 720.6854 | 720.6854 | Occupancy | 720.6854 | 720.6854 | 720.6854 | 720.6854 | 720.6854 | 720.6854
Fresh air
| Avg occ | m3/s | 9.1218 | 3.1298 | Item Outdoor Air Summary Average outdoor air occupied [m3/s] | 9.1218 | 3.1298 | 3.1345 | 3.1327 | 3.1302 | 3.1318
| Min occ | m3/s | 8.4477 | 2.1517 | Item Outdoor Air Summary Minimum outdoor air occupied [m3/s] | 8.4477 | 2.1517 | 2.0009 | 2.0921 | 2.0052 | 2.0625
| Average fresh air per area | [L/s per m2] | 1.7213 | 0.58171 | Average specifig fresh air [L/s per m2] | 1.7213 | 0.58171 | 0.58259 | 0.58225 | 0.58178 | 0.58208
| Min fresh air per area | [L/s per m2] | 1.5941 | 2.7532 | Min fresh air per area | 1.5941 | 2.7532 | 2.5603 | 2.6769 | 2.5658 | 2.6391
| Avg fresh air per pers | [L/s per pers] | 12.6571 | 4.3428 | Average fresh per person | 12.6571 | 4.3428 | 4.3494 | 4.3469 | 4.3434 | 4.3456
| Min fresh air per pers | [L/s per pers] | 11.7218 | 2.9856 | Min fresh per pers | 11.7218 | 2.9856 | 2.7764 | 2.9029 | 2.7824 | 2.8618
Zone sizing
| Total design cooling | w/m2 | 52.0885 | 46.5718 | Item HVAC Sizing Summary Total Calculated Design Cooling Load [W] | 276042.53 | 250572.26 | 237922.36 | 249560.13 | 236323.98 | 243594.6825
| Total user cooling | w/m2 | 59.9018 | 53.5576 | Item HVAC Sizing Summary Total User Design Cooling Load [W] | 317448.92 | 288158.09 | 273610.72 | 286994.15 | 271772.58 | 280133.885
| Sizing |  | 1.15 | 1.15 |  | #N/A | #N/A | #N/A | #N/A | #N/A
| Total design heating | w/m2 | 31.3782 | 28.7106 | Item HVAC Sizing Summary Total Calculated Design Heating Load [W] | 166288.44 | 154472.72 | 154231.68 | 154491.36 | 154239.91 | 154358.9175
| Total user heating | w/m2 | 39.2228 | 35.8882 | Item HVAC Sizing Summary Total User Design Heating Load [W] | 207860.6 | 193090.93 | 192789.7 | 193114.23 | 192799.85 | 192948.6775
| Sizing |  | 1.25 | 1.25 | Item HVAC Sizing Summary Total Calculated Design Cooling Air Flow [m3/s] | 22.076 | 18.619 | 17.676 | 18.546 | 17.557 | 18.0995
[5 empty] | Item HVAC Sizing Summary Total User Design Cooling Air Flow [m3/s] | 25.814 | 21.416 | 20.338 | 21.329 | 20.201 | 20.821
[5 empty] | Item HVAC Sizing Summary Total Calculated Design Heating Air Flow [m3/s] | 4.708 | 11.586 | 11.567 | 11.586 | 11.568 | 11.5767
[5 empty] | Item HVAC Sizing Summary Total User Design Heating Air Flow [m3/s] | 8.765 | 14.547 | 14.521 | 14.545 | 14.522 | 14.5337
OBSELETE |  |  |  |  | Item Lighting Average LPD [W/m2] | 9.0719 | 10.8766 | 10.8766 | 10.8766 | 10.8766 | 10.8766
| Glass U |  | 0.78 | 2.493 | Item Envelope Summary Average glass U-Factor [W/m2-K] | 0.78 | 2.493 | 2.493 | 2.493 | 2.493 | 2.493

## Sensible breakdown
|  | Proposed | Baseline | Baseline2 | Baseline3 | Baseline4 | Baseline
|  | MWh | MWh | MWh | MWh | MWh
Sensible summary HVAC Input Sensible Air Heating [GJ] [GJ] | Air heating | 74.7741 | 109.6546 | 108.2022 | 109.4077 | 107.3283 | 108.6482
Sensible summary HVAC Input Sensible Air Cooling [GJ] [GJ] | Air cooling | -341.5841 | -448.2622 | -442.1226 | -448.834 | -441.0237 | -445.0606
Sensible summary HVAC Input Heated Surface Heating [GJ] [GJ] | Surface heating | 7.0605 | 0 | 0 | 0 | 0 | 0
Sensible summary HVAC Input Cooled Surface Cooling [GJ] [GJ] | Surface cooling | -345.566 | 0 | 0 | 0 | 0 | 0
Sensible summary People Sensible Heat Addition [GJ] [GJ] | People | 43.2198 | 112.0661 | 111.5915 | 112.0003 | 111.5799 | 111.8094
Sensible summary Lights Sensible Heat Addition [GJ] [GJ] | Lights | 161.9438 | 194.9243 | 194.9243 | 194.9243 | 194.9243 | 194.9243
Sensible summary Equipment Sensible Heat Addition [GJ] [GJ] | Equipment | 204.3208 | 204.3208 | 204.3208 | 204.3208 | 204.3208 | 204.3208
Sensible summary Window Heat Addition [GJ] [GJ] | Window heat | 210.937 | 236.3399 | 233.739 | 237.5532 | 233.9959 | 235.407
Sensible summary Interzone Air Transfer Heat Addition [GJ] [GJ] | Interzone heat | 0 | 0 | 0 | 0 | 0 | 0
Sensible summary Infiltration Heat Addition [GJ] [GJ] | Infiltration heat | 0 | 1.3832 | 1.3843 | 1.3849 | 1.3791 | 1.3829
Sensible summary Opaque Surface Conduction and Other Heat Addition [GJ] [GJ] | Surface condution heat | 228.6568 | 8.9225 | 8.7473 | 8.8539 | 8.6542 | 8.7945
Sensible summary Equipment Sensible Heat Removal [GJ] [GJ] | Equipment cooling | 0 | 0 | 0 | 0 | 0 | 0
Sensible summary Window Heat Removal [GJ] [GJ] | Window cooling | -113.8006 | -211.5352 | -212.2669 | -211.4658 | -212.4441 | -211.928
Sensible summary Interzone Air Transfer Heat Removal [GJ] [GJ] | Interzone cooling | 0 | 0 | 0 | 0 | 0 | 0
Sensible summary Infiltration Heat Removal [GJ] [GJ] | Infiltration cooling | -45.8252 | -83.3244 | -83.6016 | -83.3367 | -83.6735 | -83.484
Sensible summary Opaque Surface Conduction and Other Heat Removal [GJ] [GJ] | Surface cooling | -84.1453 | -124.4899 | -124.9183 | -124.8089 | -125.0411 | -124.8146

## <Testing>
Key | Column | Value
LEED Summary Space Heating Additional Energy Use [GJ] | Baseline3 | 263.0791
| Header text | Returns column number of matched text
Test MATCH | Baseline | 5
Row text
#N/A