## Templates
General |  |  |  |  | Naming |  |  |  | Pointers |  |  | End
ID | Relative path | Style | Multiply this class | Insert zone name here | Insert unique name here | Define unique name here | Insert unique name here | Define unique name here | This field | Points to | This field | Points to
Run control, first 10 days | Library\SimulationParameters_10Days.idf | One
Run control, entire year | Library\SimulationParameters.idf | One
Sizing parameters | SystemTemplates\SysTemplate_SizingParams.idf | One
ComplianceRotation | Library\ComplianceRotation.idf | One
Baseline construction set | Library\ConstructionSetBaseline.idf | One
ConstructionSetADWindows | Library\ConstructionSetADWindows.idf | One
ConstructionSet100Percent | Library\ConstructionSet100Percent.idf | One
AsDesigned50percentU | Library\AsDesigned50percentU.idf | One
PackagedDxVAV | SystemTemplates\SysTemplate_PackagedDX_VAV.idf | Named N to N | HVACTemplate:Zone:VAV | //ATTR[1] | //HVACTemplate:Thermostat//ATTR[1] | VAVThermostat {Insert Name} | //PackagedVAVSystem Restaurant//ATTR[1] | PackagedVAV {Insert Name} | HVACTemplate:Zone:VAV//ATTR[2] | HVACTemplate:Thermostat//ATTR[1] | HVACTemplate:Zone:VAV//ATTR[3] | HVACTemplate:System:PackagedVAV//ATTR[1]
PTHP | SystemTemplates\SysTemplate_PTHP.idf | N to N | HVACTemplate:Zone:PTHP | //ATTR[1]
VAV template | SystemTemplates\SysTemplate_VAV.idf | N to N | HVACTemplate:Zone:VAV | //ATTR[1]
IdealLoads template | SystemTemplates\SysTemplate_IdealLoads.idf | N to N | IdealLoadsAirSystem | //ATTR[1]
Table output | Library\TableOutput.idf | One
Basic output | Library\Output.idf | One
Advanced output | Library\OutputAdvanced.idf | One

## Complex Logic
!-Generator IDFEditor 1.38a
!-Option SortedOrder
!-NOTE: All comments with '!-' are ignored by the IDFEditor and are generated automatically.
!- Use '!' comments if they need to be retained when using the IDFEditor.
!- =========== ALL OBJECTS IN CLASS: HVACTEMPLATE:THERMOSTAT =========== | Pointers
HVACTemplate:Thermostat,
VAVThermostat Restaurant, !- Name
, !- Heating Setpoint Schedule Name | Unique Names
21.1, !- Constant Heating Setpoint {C}
, !- Cooling Setpoint Schedule Name
23.8; !- Constant Cooling Setpoint {C}
!- =========== ALL OBJECTS IN CLASS: HVACTEMPLATE:ZONE:VAV ===========
HVACTemplate:Zone:VAV,
ZoneName, !- Zone Name
PackagedVAVSystem Restaurant, !- Template VAV System Name
VAVThermostat Restaurant, !- Template Thermostat Name
autosize, !- Supply Air Maximum Flow Rate {m3/s}
, !- Zone Heating Sizing Factor
, !- Zone Cooling Sizing Factor
Constant, !- Zone Minimum Air Flow Input Method
0, !- Constant Minimum Air Flow Fraction
, !- Fixed Minimum Air Flow Rate {m3/s}
, !- Minimum Air Flow Fraction Schedule Name
Flow/Person, !- Outdoor Air Method
0.00944, !- Outdoor Air Flow Rate per Person {m3/s}
, !- Outdoor Air Flow Rate per Zone Floor Area {m3/s-m2}
, !- Outdoor Air Flow Rate per Zone {m3/s}
Electric, !- Reheat Coil Type
, !- Reheat Coil Availability Schedule Name
Reverse, !- Damper Heating Action
, !- Maximum Flow per Zone Floor Area During Reheat {m3/s-m2}
, !- Maximum Flow Fraction During Reheat
, !- Maximum Reheat Air Temperature {C}
, !- Design Specification Outdoor Air Object Name
, !- Supply Plenum Name
, !- Return Plenum Name
Electric, !- Baseboard Heating Type
, !- Baseboard Heating Availability Schedule Name
autosize; !- Baseboard Heating Capacity {W}
!- =========== ALL OBJECTS IN CLASS: HVACTEMPLATE:SYSTEM:PACKAGEDVAV ===========
HVACTemplate:System:PackagedVAV,
PackagedVAVSystem Restaurant, !- Name
, !- System Availability Schedule Name
autosize, !- Supply Fan Maximum Flow Rate {m3/s}
autosize, !- Supply Fan Minimum Flow Rate {m3/s}
DrawThrough, !- Supply Fan Placement
0.7, !- Supply Fan Total Efficiency
1000, !- Supply Fan Delta Pressure {Pa}
0.9, !- Supply Fan Motor Efficiency
1, !- Supply Fan Motor in Air Stream Fraction
TwoSpeedDX, !- Cooling Coil Type
, !- Cooling Coil Availability Schedule Name
, !- Cooling Coil Setpoint Schedule Name
12.8, !- Cooling Coil Design Setpoint {C}
autosize, !- Cooling Coil Capacity {W}
autosize, !- Cooling Coil Rated Sensible Heat Ratio
3.22, !- Cooling Coil Rated COP
Electric, !- Heating Coil Type
, !- Heating Coil Availability Schedule Name
, !- Heating Coil Setpoint Schedule Name
10, !- Heating Coil Design Setpoint {C}
autosize, !- Heating Coil Capacity {W}
0.8, !- Gas Heating Coil Efficiency
, !- Gas Heating Coil Parasitic Electric Load {W}
autosize, !- Maximum Outdoor Air Flow Rate {m3/s}
0.4, !- Minimum Outdoor Air Flow Rate {m3/s}
ProportionalMinimum, !- Minimum Outdoor Air Control Type
, !- Minimum Outdoor Air Schedule Name
NoEconomizer, !- Economizer Type
NoLockout, !- Economizer Lockout
, !- Economizer Maximum Limit Dry-Bulb Temperature {C}
, !- Economizer Maximum Limit Enthalpy {J/kg}
, !- Economizer Maximum Limit Dewpoint Temperature {C}
, !- Economizer Minimum Limit Dry-Bulb Temperature {C}
, !- Supply Plenum Name
, !- Return Plenum Name
InletVaneDampers, !- Supply Fan Part-Load Power Coefficients
StayOff, !- Night Cycle Control
, !- Night Cycle Control Zone Name
None, !- Heat Recovery Type
0.7, !- Sensible Heat Recovery Effectiveness
0.65, !- Latent Heat Recovery Effectiveness
None, !- Cooling Coil Setpoint Reset Type
None, !- Heating Coil Setpoint Reset Type
None, !- Dehumidification Control Type
, !- Dehumidification Control Zone Name
60, !- Dehumidification Setpoint {percent}
None, !- Humidifier Type
, !- Humidifier Availability Schedule Name
0.000001, !- Humidifier Rated Capacity {m3/s}
2690, !- Humidifier Rated Electric Power {W}
, !- Humidifier Control Zone Name
30; !- Humidifier Setpoint {percent}

## Sheet3
Multiply 1 over N zones
Unique name for 1 to N | Gym VAV
Zones to Multiply Over | Gym
!- =========== ALL OBJECTS IN CLASS: HVACTEMPLATE:ZONE:IDEALLOADSAIRSYSTEM ===========
HVACTemplate:Zone:IdealLoadsAirSystem,
ZoneName, !- Zone Name
IdealLoadsThermostat; !- Template Thermostat Name
Just once
!- =========== ALL OBJECTS IN CLASS: OUTPUT:VARIABLEDICTIONARY ===========
Output:VariableDictionary,
regular; !- Key Field
Multiply N over N zones
Unique names | {ZoneName} People
People,
Zone {38} People, ! Name
Zone {38}, ! Zone or ZoneList Name
Hotel Occupancy, ! Number of People Schedule Name
People/Area, ! Number of People Calculation Method
, ! Number of People
0.040000000000000001, ! People per Zone Floor Area
, ! Zone Floor Area per Person
0.3, ! Fraction Radiant
, ! Sensible Heat Fraction
Office Activity Schedule, ! Activity Level Schedule Name
Multiply M over N zones
Unique names | {ZoneName} People
People,
Zone {38} People, ! Name
Zone {38}, ! Zone or ZoneList Name
Hotel Occupancy, ! Number of People Schedule Name
People/Area, ! Number of People Calculation Method
, ! Number of People
0.040000000000000001, ! People per Zone Floor Area
, ! Zone Floor Area per Person
0.3, ! Fraction Radiant
, ! Sensible Heat Fraction
Office Activity Schedule, ! Activity Level Schedule Name