## Schedule
RESIDENTIAL
|  |  |  | Occupancy |  |  | Lighting and receptacle
|  |  | Hour | Wk | Sat | Sun | Wk | Sat | Sun
|  |  | 1 | 90 | 90 | 70 | 20
|  |  | 2 | 90 | 90 | 70 | 15
|  |  | 3 | 90 | 90 | 70 | 10
|  |  | 4 | 90 | 90 | 70 | 10
|  |  | 5 | 90 | 90 | 70 | 10
|  |  | 6 | 90 | 90 | 70 | 20
|  |  | 7 | 70 | 70 | 70 | 40
|  |  | 8 | 40 | 50 | 70 | 50
|  |  | 9 | 40 | 50 | 50 | 40
|  |  | 10 | 20 | 30 | 50 | 40
|  |  | 11 | 20 | 30 | 50 | 25
|  |  | 12 | 20 | 30 | 30 | 25
|  |  | 13 | 20 | 30 | 30 | 25
|  |  | 14 | 20 | 30 | 20 | 25
|  |  | 15 | 20 | 30 | 20 | 25
|  |  | 16 | 30 | 30 | 20 | 25
|  |  | 17 | 50 | 30 | 30 | 25
|  |  | 18 | 50 | 50 | 40 | 25
|  |  | 19 | 50 | 60 | 40 | 60
|  |  | 20 | 70 | 60 | 60 | 80
|  |  | 21 | 70 | 60 | 60 | 90
|  |  | 22 | 80 | 70 | 80 | 80
|  |  | 23 | 90 | 70 | 80 | 60
|  |  | 24 | 90 | 70 | 80 | 30
OFFICE
Table C-5 – Office Occupancy
Source: Table G-I, User’s Manual for ANSI/ASHRAE/IESNA Standard 90.1-2007
|  |  |  | Occupancy |  |  | Lighting and receptacle
|  |  | Hour | Werktag | Wochenende |  | Werktag | Wochenende
| Setback 18 | 0 | 1 | 0 | 0 | 1 | 5 | 5
| Setback 18 | 1 | 2 | 0 | 0 | 2 | 5 | 5
| Setback 18 | 2 | 3 | 0 | 0 | 3 | 5 | 5
| Setback 18 | 3 | 4 | 0 | 0 | 4 | 5 | 5
| Setback 18 | 4 | 5 | 0 | 0 | 5 | 5 | 5
| Setback 18 | 5 | 6 | 0 | 0 | 6 | 10 | 5
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 6 | 7 | 10 | 10 | 7 | 10 | 10
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 7 | 8 | 20 | 10 | 8 | 30 | 10
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 8 | 9 | 95 | 30 | 9 | 90 | 30
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 9 | 10 | 95 | 30 | 10 | 90 | 30
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 10 | 11 | 95 | 30 | 11 | 90 | 30
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 11 | 12 | 95 | 30 | 12 | 90 | 30
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 12 | 13 | 50 | 10 | 13 | 90 | 15
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 13 | 14 | 95 | 10 | 14 | 90 | 15
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 14 | 15 | 95 | 10 | 15 | 90 | 15
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 15 | 16 | 95 | 10 | 16 | 90 | 15
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 16 | 17 | 95 | 10 | 17 | 90 | 15
Luft 66.5m3_hr ACH 22C | heat on - 21 C | 17 | 18 | 30 | 5 | 18 | 50 | 5
| Setback 18 | 18 | 19 | 10 | 5 | 19 | 30 | 5
| Setback 18 | 19 | 20 | 10 | 0 | 20 | 30 | 5
| Setback 18 | 20 | 21 | 10 | 0 | 21 | 20 | 5
| Setback 18 | 21 | 22 | 10 | 0 | 22 | 20 | 5
| Setback 18 | 22 | 23 | 5 | 0 | 23 | 10 | 5
| Setback 18 | 23 | 24 | 5 | 0 | 24 | 5 | 5
Note on C49: ANON:

## Modeling Data
| 1 - Lighting |  |  |  | 2 - Plug Loads | [6 empty] | 3 - Occupancy | [8 empty] | 4 - Outdoor Air |  |  | 5 - Water Heating |  |  | 6 - Process |  | 7 - Schedules
| Allowed Lighting Power Density |  |  |  | Default Receptacle Power Density |  |  |  | Receptacle Power Coefficients |  |  | Occupant Density |  |  |  | Heat Gain per Occupant (Btu/occ) |  |  |  |  | Minimum Ventilation |  |  | Load | Load | DHW | Interior Gas Appliance Power Density | Refrigeration Power Density
| ASHRAE Standard 90.1-2001 |  | ASHRAE Standard 90.1-2007 | W/m2 | California 2005 ACM |  | COMNET |  | C | Pdmisc | D | California 2005 ACM |  | COMNET |  | Sensible |  | Latent |  |  | California 2005 ACM |  | COMNET | California 2005 ACM | COMNET | DHW |  |  | California 2005 Schedule | COMNET Schedule
| (W/ft²) | W/m2 | (W/ft²) | W/m2 | (W/ft²) | W/m2 | (W/ft²) | W/m2 |  |  |  | (ft³/person) | pers/100m2 | (ft³/person) | pers/100m2 | Btu/hr/occ | W/occ | Btu/hr/occ | W/occ | kg/hr water | (cfm/ft²) | L/s/m2 |  | (Btu/h-occ) | (G/day-occ) | L/day.occ | (Btu/h-ft²) | (W/ft²)
Whole Building Categories |  | 0
Auto Repair | 1.5 | 16.14 | 0.9 | 9.684 | 1 | 10.76 | 0.64584 | 6.9493 | 2 | 0.54813 | 0.943 | 142.8571 | 7.532 | 143 | 7.5245 | 375 | 109.8281 | 625 | 183.0469 | 0.26853 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.22 | 0.15 | Non-Residential | Table G-H Light Manufacturing Occupancy
College/ University | 1.5 | 16.14 | 1.2 | 12.912 | 1 | 10.76 | N/A | #VALUE! | 2 | N/A | 0.773 | 25 | 43.04 | 50 | 21.52 | 246 | 72.0473 | 171 | 50.0816 | 0.073469 | 0.32 |  | 0.32 | 108 | 0.60766 | 2.3002 | N/A | N/A | Non-Residential | Table G-M School Occupancy
Convention Center | 1.4 | 15.064 | 1.2 | 12.912 | 0.96 | 10.3296 | 1.0878 | 11.7048 | 2 | 0.54813 | 0.779 | 7.3529 | 146.336 | 9 | 119.5556 | 245 | 71.7544 | 112 | 32.802 | 0.04812 | 1.02 |  | 1.02 | 57 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Court House | 1.4 | 15.064 | 1.2 | 12.912 | 1 | 10.76 | 1.0878 | 11.7048 | 2 | 0.54813 | 0.923 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Dining, Bar/Coctail Lounge | 1.5 | 16.14 | 1.3 | 13.988 | 0.79 | 8.5004 | 1.5282 | 16.4438 | 2 | 0.92903 | 1 | 22.2222 | 48.42 | 30 | 35.8667 | 274 | 80.2477 | 334 | 97.8203 | 0.1435 | 0.38 |  | 0.38 | 366 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dining, Cafeteria/Fast Food | 1.8 | 19.368 | 1.4 | 15.064 | 0.79 | 8.5004 | 1.5282 | 16.4438 | 2 | 0.92903 | 1 | 22.2222 | 48.42 | 30 | 35.8667 | 274 | 80.2477 | 334 | 97.8203 | 0.1435 | 0.38 |  | 0.38 | 366 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dining, Family | 1.9 | 20.444 | 1.6 | 17.216 | 0.79 | 8.5004 | 1.5282 | 16.4438 | 2 | 0.92903 | 1 | 22.2222 | 48.42 | 30 | 35.8667 | 274 | 80.2477 | 334 | 97.8203 | 0.1435 | 0.38 |  | 0.38 | 366 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dormitory | 1.5 | 16.14 | 1 | 10.76 | 0.5 | 5.38 | 1.2598 | 13.5555 | 2 | 0.29729 | 0.565 | 100 | 10.76 | 150 | 7.1733 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | N/A | 120 | Note 1 | #VALUE! | 0.2 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Exercise Center | 1.4 | 15.064 | 1 | 10.76 | 1 | 10.76 | 1.8632 | 20.0477 | 2 | 0.54813 | 0.779 | 100 | 10.76 | 50 | 21.52 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.09 | 0.12 | Non-Residential | N/A
Gymnasium | 1.7 | 18.292 | 1.1 | 11.836 | 1 | 10.76 | 1.8632 | 20.0477 | 2 | 0.54813 | 0.779 | 100 | 10.76 | 50 | 21.52 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.09 | 0.12 | Non-Residential | N/A
Health Care Clinic | 1.6 | 17.216 | 1 | 10.76 | 1.18 | 12.6968 | 1.9917 | 21.4309 | 2 | 0.76181 | 0.962 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 213 | 62.3824 | 0.091514 | 0.15 |  | 0.15 | 110 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Hospital | 1.6 | 17.216 | 1.2 | 12.912 | 1.18 | 12.6968 | 1.9917 | 21.4309 | 2 | 0.76181 | 0.68 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 213 | 62.3824 | 0.091514 | 0.15 |  | 0.15 | 110 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Hotel | 1.7 | 18.292 | 1 | 10.76 | 0.5 | 5.38 | 1.2598 | 13.5555 | 2 | 0.29729 | 0.565 | 200 | 5.38 | 200 | 5.38 | 245 | 71.7544 | 155 | 45.3956 | 0.066595 | 0.15 |  | N/A | 2800 | Note 1 | #VALUE! | 0.2 | 0.08 | Hotel Function | Table G-G Hotel/Motel Occupancy
K-12 School | 1.5 | 16.14 | 1.2 | 12.912 | 1 | 10.76 | 1.0218 | 10.9945 | 2 | 0.18581 | 0.773 | 25 | 43.04 | 25 | 43.04 | 246 | 72.0473 | 171 | 50.0816 | 0.073469 | 0.32 |  | 0.32 | 108 | 0.61 | 2.3091 | 0.04 | 0.03 | Non-Residential | Table G-M School Occupancy
Library | 1.5 | 16.14 | 1.3 | 13.988 | 1.5 | 16.14 | 1.0218 | 10.9945 | 2 | 0.18581 | 0.779 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | 0.18 | 0.68137 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Manufacturing Facility | 2.2 | 23.672 | 1.3 | 13.988 | 1 | 10.76 | 0.44728 | 4.8127 | 2 | 0.18581 | 1 | 142.8571 | 7.532 | 200 | 5.38 | 375 | 109.8281 | 625 | 183.0469 | 0.26853 | 0.15 |  | 0.15 | 120 | 0.60766 | 2.3002 | 0 | 0.28 | Non-Residential | Table G-H Light Manufacturing Occupancy
Motel | 2 | 21.52 | 1 | 10.76 | 0.5 | 5.38 | 1.2598 | 13.5555 | 2 | 0.29729 | 0.565 | 200 | 5.38 | 200 | 5.38 | 245 | 71.7544 | 155 | 45.3956 | 0.066595 | 0.15 |  | N/A | 2800 | Note 1 | #VALUE! | 0.2 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Motion Picture Theatre | 1.6 | 17.216 | 1.2 | 12.912 | 0.54 | 5.8104 | 1.0878 | 11.7048 | 2 | 0.54813 | 0.779 | 7.6923 | 139.88 | 9 | 119.5556 | 268 | 78.4905 | 403 | 118.0286 | 0.17315 | 0.98 |  | 0.98 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Multi-Family | 1 | 10.76 | 0.7 | 7.532 | 0.5 | 5.38 | 1.4403 | 15.4973 | 2 | 0.29729 | 1 | 100 | 10.76 | 150 | 7.1733 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | Note 2 | #VALUE! | 0.2 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Museum- General | 1.6 | 17.216 | 1.1 | 11.836 | 1 | 10.76 | 1.0878 | 11.7048 | 2 | 0.54813 | 0.779 | 142.8571 | 7.532 | 50 | 21.52 | 375 | 109.8281 | 625 | 183.0469 | 0.26853 | 0.15 |  | 0.15 | 120 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Office | 1.3 | 13.988 | 1 | 10.76 | 1.34 | 14.4184 | 2.4727 | 26.6063 | 2 | 0.7711 | 0.923 | 100 | 10.76 | 150 | 7.1733 | 250 | 73.2188 | 206 | 60.3323 | 0.088507 | 0.15 |  | 0.15 | 106 | 1.004 | 3.8004 | 0.04 | 0.06 | Non-Residential | Table G-I Office Occupancy
Parking Garage | 0.3 | 3.228 | 0.3 | 3.228 | 1 | 10.76 | N/A | #VALUE! | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 0 | 0 | 0 | 0 | Retail | Table G-J Parking Garage Occupancy
Penitentiary | 1.2 | 12.912 | 1 | 10.76 | 0.5 | 5.38 | 1.2598 | 13.5555 | 2 | 0.29729 | 0.565 | 100 | 10.76 | 250 | 4.304 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | Note 1 | #VALUE! | 0.2 | 0.08 | Residential | N/A
Performing Arts Theatre | 1.5 | 16.14 | 1.6 | 17.216 | 0.54 | 5.8104 | 1.0878 | 11.7048 | 2 | 0.54813 | 0.779 | 7.6923 | 139.88 | 9 | 119.5556 | 268 | 78.4905 | 403 | 118.0286 | 0.17315 | 0.98 |  | 0.98 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Police/Fire Station | 1.3 | 13.988 | 1 | 10.76 | 1.34 | 14.4184 | 1.9145 | 20.5997 | 2 | 1.1148 | 0.627 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 206 | 60.3323 | 0.088507 | 0.15 |  | 0.15 | 106 | 1.004 | 3.8004 | 0.09 | 2.6 | Non-Residential | N/A
Post Office | 1.6 | 17.216 | 1.1 | 11.836 | 1 | 10.76 | 1 | 10.76 | 2 | 0.7711 | 0.963 | 142.8571 | 7.532 | 100 | 10.76 | 375 | 109.8281 | 625 | 183.0469 | 0.26853 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.04 | 0.06 | Non-Residential | Table G-I Office Occupancy
Religious Building | 2.2 | 23.672 | 1.3 | 13.988 | 0.96 | 10.3296 | 0.41236 | 4.437 | 2 | 0.54813 | 0.972 | 7.3529 | 146.336 | 9 | 119.5556 | 245 | 71.7544 | 112 | 32.802 | 0.04812 | 1.03 |  | 1.03 | 57 | 0.2642 | 1.0001 | 0.04 | 1.53 | Non-Residential | Table G-E Assembly Occupancy
Retail | 1.9 | 20.444 | 1.5 | 16.14 | 0.5 | 5.38 | 0.85621 | 9.2128 | 2 | 0.34374 | 0.963 | 30.303 | 35.508 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | N/A | 120 | 0.60766 | 2.3002 | 0.03 | 0.14 | Retail | Table G-L Retail Occupancy
Sports Arena | 1.5 | 16.14 | 1.1 | 11.836 | 1 | 10.76 | 1.0878 | 11.7048 | 2 | 0.54813 | 0.779 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Town Hall | 1.4 | 15.064 | 1.1 | 11.836 | 1 | 10.76 | 1.0878 | 11.7048 | 2 | 0.54813 | 0.779 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transportation | 1.2 | 12.912 | 1 | 10.76 | 1 | 10.76 | 1.8632 | 20.0477 | 2 | 0.54813 | 0.839 | 100 | 10.76 | 60 | 17.9333 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.09 | 0.12 | Non-Residential | Table G-E Assembly Occupancy
Warehouse | 1.2 | 12.912 | 0.8 | 8.608 | 1 | 10.76 | 0.44728 | 4.8127 | 2 | 0.18581 | 1 | 142.8571 | 7.532 | 333 | 3.2312 | 375 | 109.8281 | 625 | 183.0469 | 0.26853 | 0.15 |  | 0.15 | 120 | 0.60766 | 2.3002 | 0 | 0.28 | Non-Residential | Table G-N Warehouse Occupancy
Workshop | 1.7 | 18.292 | 1.4 | 15.064 | 1 | 10.76 | 0.44728 | 4.8127 | 2 | 0.18581 | 0.943 | 142.8571 | 7.532 | 200 | 5.38 | 375 | 109.8281 | 625 | 183.0469 | 0.26853 | 0.15 |  | 0.15 | 120 | 0.60766 | 2.3002 | 0 | 0.28 | Non-Residential | Table G-H Light Manufacturing Occupancy
Space-by-Space Classifications |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | #DIV/0! |  | #DIV/0! |  | 0 |  | 0 | 0 | [5 empty] | 0
Atrium (Floors 1-3) | 1.3 | 13.988 | 0.6 | 6.456 | 0.5 | 5.38 | 0.5 | 5.38 | N/A | N/A | N/A | 30.303 | 35.508 | 60 | 17.9333 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | 0.25 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-L Retail Occupancy
Atrium (Floors 4+) | 0.2 | 2.152 | 0.2 | 2.152 | 0.5 | 5.38 | 0.5 | 5.38 | N/A | N/A | N/A | 30.303 | 35.508 | 60 | 17.9333 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | 0.25 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-L Retail Occupancy
Auditorium, Exercise Center | 0.5 | 5.38 | 0.3 | 3.228 | 0.5 | 5.38 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 50 | 21.52 | 50 | 21.52 | 255 | 74.6831 | 875 | 256.2656 | 0.37594 | 0.15 |  | 0.15 | 120 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Auditorium, General | 1.6 | 17.216 | 0.9 | 9.684 | 1 | 10.76 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Auditorium, Gymnasium | 0.5 | 5.38 | 0.4 | 4.304 | 0.5 | 5.38 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 50 | 21.52 | 50 | 21.52 | 255 | 74.6831 | 875 | 256.2656 | 0.37594 | 0.15 |  | 0.15 | 120 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Auditorium, Indoor Sports Arena | 0.5 | 5.38 | 0.4 | 4.304 | 1 | 10.76 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Auditorium, Penitentairy | 1.9 | 20.444 | 0.7 | 7.532 | 1 | 10.76 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Auditorium, Religious Worship | 3.2 | 34.432 | 1.7 | 18.292 | 0.5 | 5.38 | 0.41236 | 4.437 | 2 | 0.54813 | 0.4 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 1.53 | Non-Residential | Table G-E Assembly Occupancy
Automotive Repair | 1.4 | 15.064 | 0.7 | 7.532 | 1 | 10.76 | 0.99552 | 10.7117 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 1.5 |  | 1.5 | 120 | 1.004 | 3.8004 | 0.22 | 0.15 | Non-Residential | Table G-H Light Manufacturing Occupancy
Bank | 2.4 | 25.824 | 1.5 | 16.14 | 1.5 | 16.14 | 2.6864 | 28.9055 | 2 | 0.7711 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.04 | 0.06 | Non-Residential | Table G-I Office Occupancy
Civic, Confinement Cells | 1.1 | 11.836 | 0.9 | 9.684 | 0.2 | 2.152 | 2.0284 | 21.8261 | 2 | 1.1148 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 1.004 | 3.8004 | 0.09 | 2.6 | Residential | N/A
Civic, Courtroom | 2.1 | 22.596 | 1.9 | 20.444 | 1.5 | 16.14 | 2.0284 | 21.8261 | 2 | 1.1148 | 1 | 40 | 26.9 | 40 | 26.9 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.19 |  | 0.19 | 120 | 1.004 | 3.8004 | 0.09 | 2.6 | Non-Residential | Table G-E Assembly Occupancy
Civic, Judge's Chambers | 1.1 | 11.836 | 1.3 | 13.988 | 1.5 | 16.14 | 2.3944 | 25.764 | 2 | 0.7711 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.04 | 0.06 | Non-Residential | N/A
Classroom/Lecture/Training, General | 1.6 | 17.216 | 1.4 | 15.064 | 1 | 10.76 | 0.87793 | 9.4465 | 2 | 0.14865 | 1 | 20 | 53.8 | 20 | 53.8 | 245 | 71.7544 | 155 | 45.3956 | 0.066595 | 0.38 |  | 0.38 | 120 | Note 3 | #VALUE! | 0.04 | 0.03 | Non-Residential | Table G-M School Occupancy
Classroom/Lecture/Training, Penitentairy | 1.4 | 15.064 | 1.3 | 13.988 | 1 | 10.76 | 1.2249 | 13.1797 | 2 | 0.18581 | 1 | 20 | 53.8 | 20 | 53.8 | 245 | 71.7544 | 155 | 45.3956 | 0.066595 | 0.38 |  | 0.38 | 120 | Note 3 | #VALUE! | 0.04 | 0.03 | Non-Residential | N/A
Conference/Meeting | 1.5 | 16.14 | 1.3 | 13.988 | 1 | 10.76 | 1.1896 | 12.8006 | 2 | 0.54813 | 1 | 14.9254 | 72.092 | 15 | 71.7333 | 245 | 71.7544 | 155 | 45.3956 | 0.066595 | 0.5 |  | 0.5 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Convention Center | 0.5 | 5.38 | 0.7 | 7.532 | 1 | 10.76 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Corridor/Transition, General | 0.7 | 7.532 | 0.5 | 5.38 | 0.2 | 2.152 | 0.77995 | 8.3923 | 2 | 0.54813 | 1 | 100 | 10.76 | 200 | 5.38 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 0 | 0 | 0 | 0 | Non-Residential | N/A
Corridors/Tranistions, Hospital | 1.6 | 17.216 | 1 | 10.76 | 0.2 | 2.152 | 0.77995 | 8.3923 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 0 | 0 | 0 | 0 | Non-Residential | Table G-F Health Occupancy
Corridors/Tranistions, Manufacturing | 0.5 | 5.38 | 0.5 | 5.38 | 0.2 | 2.152 | 0.77995 | 8.3923 | 2 | 0.54813 | 1 | 100 | 10.76 | 200 | 5.38 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 0 | 0 | 0 | 0 | Non-Residential | Table G-H Light Manufacturing Occupancy
Dining, Bar/Coctail Lounge | 1.2 | 12.912 | 1.4 | 15.064 | 1 | 10.76 | 1.5287 | 16.4483 | 2 | 0.92903 | 1 | 14.9254 | 72.092 | 30 | 35.8667 | 275 | 80.5406 | 275 | 80.5406 | 0.11815 | 0.5 |  | 0.5 | 120 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dining, Family Dining/Restaurant | 2.2 | 23.672 | 2.1 | 22.596 | 0.5 | 5.38 | 1.5287 | 16.4483 | 2 | 0.92903 | 1 | 14.9254 | 72.092 | 30 | 35.8667 | 275 | 80.5406 | 275 | 80.5406 | 0.11815 | 0.5 |  | 0.5 | 385 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dining, General | 1.4 | 15.064 | 0.9 | 9.684 | 0.5 | 5.38 | 1.5287 | 16.4483 | 2 | 0.92903 | 1 | 14.9254 | 72.092 | 30 | 35.8667 | 275 | 80.5406 | 275 | 80.5406 | 0.11815 | 0.5 |  | 0.5 | 385 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dining, Hotel | 1 | 10.76 | 1.3 | 13.988 | 0.5 | 5.38 | 1.5627 | 16.8144 | 2 | 0.92903 | 1 | 14.9254 | 72.092 | 30 | 35.8667 | 275 | 80.5406 | 275 | 80.5406 | 0.11815 | 0.5 |  | 0.5 | 385 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dining, Motel | 1.2 | 12.912 | 1.2 | 12.912 | 0.5 | 5.38 | 1.5627 | 16.8144 | 2 | 0.92903 | 1 | 14.9254 | 72.092 | 30 | 35.8667 | 275 | 80.5406 | 275 | 80.5406 | 0.11815 | 0.5 |  | 0.5 | 385 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dinning, Penitentiary Cafeteria | N/A | #VALUE! | 1.3 | 13.988 | 0.5 | 5.38 | 1.5627 | 16.8144 | 2 | 0.92903 | 1 | 14.9254 | 72.092 | 15 | 71.7333 | 275 | 80.5406 | 275 | 80.5406 | 0.11815 | 0.5 |  | 0.5 | 385 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Dormitory/Living Quarters | 1.9 | 20.444 | 1.1 | 11.836 | 0.5 | 5.38 | 1.4403 | 15.4973 | 2 | 0.29729 | 1 | 100 | 10.76 | 150 | 7.1733 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | Note 1 | #VALUE! | 0.2 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Dressing/Locker Rooms | 0.8 | 8.608 | 0.6 | 6.456 | 0.5 | 5.38 | 0.82633 | 8.8913 | 2 | 0.54813 | 1 | 50 | 21.52 | 50 | 21.52 | 255 | 74.6831 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 385 | N/A | #VALUE! | N/A | N/A | Non-Residential | 0
Electrical/Mechanical Room | 1.3 | 13.988 | 1.5 | 16.14 | 0.2 | 2.152 | 0.2 | 2.152 | N/A | N/A | N/A | 333.3333 | 3.228 | 750 | 1.4347 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 0 | 0 | 0 | 0 | Non-Residential | N/A
Equipment Room | 0.8 | 8.608 | 1.2 | 12.912 | 0.2 | 2.152 | 0.2 | 2.152 | N/A | N/A | N/A | 333.3333 | 3.228 | 750 | 1.4347 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | N/A | #VALUE! | N/A | N/A | Non-Residential | N/A
Exhibit Space, Conference | 3.3 | 35.508 | 1.3 | 13.988 | 1 | 10.76 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 14.9254 | 72.092 | 30 | 35.8667 | 245 | 71.7544 | 155 | 45.3956 | 0.066595 | 0.5 |  | 0.5 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Fire Station, Engine Room | 0.9 | 9.684 | 0.8 | 8.608 | 1.5 | 16.14 | 1.8223 | 19.6081 | 2 | 1.1148 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.09 | 2.6 | Non-Residential | N/A
Fire Station, Sleeping Quarters | 1.1 | 11.836 | 0.3 | 3.228 | 0.5 | 5.38 | 1.8223 | 19.6081 | 2 | 1.1148 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | N/A | #VALUE! | N/A | N/A | Residential | N/A
Food Preparation/ Industrial Kitchen | 2.2 | 23.672 | 1.2 | 12.912 | 1.5 | 16.14 | 1.5627 | 16.8144 | 2 | 0.92903 | 1 | 200 | 5.38 | 200 | 5.38 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 385 | 10.0396 | 38.004 | 5.14 | 0.06 | Non-Residential | Table G-K Restaurant Occupancy
Gym, Exercise Area | 1.1 | 11.836 | 0.9 | 9.684 | 0.5 | 5.38 | 0.82633 | 8.8913 | 2 | 0.54813 | 1 | 50 | 21.52 | 50 | 21.52 | 255 | 74.6831 | 875 | 256.2656 | 0.37594 | 0.15 |  | 0.15 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | 0
Gym, Playing Area | 1.9 | 20.444 | 1.4 | 15.064 | 0.5 | 5.38 | 0.82633 | 8.8913 | 2 | 0.54813 | 1 | 50 | 21.52 | 50 | 21.52 | 255 | 74.6831 | 875 | 256.2656 | 0.37594 | 0.15 |  | 0.15 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | 0
Home Nursing/Senior Housing | 2.5 | 26.9 | 1.1 | 11.836 | 0.5 | 5.38 | 1.9482 | 20.9624 | 2 | 1.1148 | 1 | 100 | 10.76 | 200 | 5.38 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | 3.0119 | 11.4012 | 0.33 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Hospital, Waiting Area | N/A | #VALUE! | 0.8 | 8.608 | 0.5 | 5.38 | 0.82633 | 8.8913 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-F Health Occupancy
Hotel/ Motel Guest Rooms | 2.5 | 26.9 | 1.1 | 11.836 | 0.5 | 5.38 | 1.2415 | 13.3581 | 2 | 0.29729 | 1 | 200 | 5.38 | 200 | 5.38 | 245 | 71.7544 | 155 | 45.3956 | 0.066595 | 0.15 |  | 0.15 | 2800 | Note 1 | #VALUE! | 0.2 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Laboratory | 1.8 | 19.368 | 1.4 | 15.064 | 1 | 10.76 | 3.9641 | 42.6541 | 2 | 2.7871 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.38 |  | 0.38 | 120 | 10.0396 | 38.004 | 3.72 | 0.06 | Non-Residential | Table G-O Laboratory Occupancy
Laundry Facility | 0.7 | 7.532 | 0.6 | 6.456 | 3 | 32.28 | 3 | 32.28 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 385 | 1.004 | 3.8004 | 0.22 | 0.15 | Non-Residential | Table G-L Retail Occupancy
Library, Cataloging | 1.4 | 15.064 | 1.1 | 11.836 | 1.5 | 16.14 | 1.5369 | 16.5369 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | Note 3 | #VALUE! | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Library, Reading Area | 1.8 | 19.368 | 1.2 | 12.912 | 1.5 | 16.14 | 1.5369 | 16.5369 | 2 | 0.54813 | 1 | 50 | 21.52 | 50 | 21.52 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | Note 3 | #VALUE! | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Library, Stacks | 1.9 | 20.444 | 1.7 | 18.292 | 1.5 | 16.14 | 1.5369 | 16.5369 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | Note 3 | #VALUE! | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Lobby, General | 1.8 | 19.368 | 1.3 | 13.988 | 0.5 | 5.38 | 1 | 10.76 | N/A | N/A | N/A | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 60 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-E Assembly Occupancy
Lobby, Hotel | 1.7 | 18.292 | 1.1 | 11.836 | 0.5 | 5.38 | 1.2415 | 13.3581 | 2 | 0.29729 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 120 | 0 | 0 | 0.2 | 0.08 | Residential | Table G-G Hotel/Motel Occupancy
Lobby, Motion Picture Theatre | 0.8 | 8.608 | 1.1 | 11.836 | 0.5 | 5.38 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Lobby, Performing Arts Theatre | 1.2 | 12.912 | 3.3 | 35.508 | 0.5 | 5.38 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Lounge/Recreation | 1.4 | 15.064 | 1.2 | 12.912 | 1 | 10.76 | 0.82633 | 8.8913 | 2 | 0.54813 | 1 | 14.9254 | 72.092 | 100 | 10.76 | 275 | 80.5406 | 275 | 80.5406 | 0.11815 | 0.5 |  | 0.5 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Manufacturing, High Bay | 3 | 32.28 | 1.7 | 18.292 | 1 | 10.76 | 1 | 10.76 | N/A | N/A | N/A | 100 | 10.76 | 200 | 5.38 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, Low Bay | 2.1 | 22.596 | 1.2 | 12.912 | 1 | 10.76 | 1 | 10.76 | N/A | N/A | N/A | 100 | 10.76 | 200 | 5.38 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-H Light Manufacturing Occupancy
Manufacturing, Precision | 6.2 | 66.712 | 2.1 | 22.596 | 1 | 10.76 | 1 | 10.76 | N/A | N/A | N/A | 100 | 10.76 | 200 | 5.38 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-H Light Manufacturing Occupancy
Mechanical Control Room | 0.5 | 5.38 | 0.5 | 5.38 | 0.2 | 2.152 | 0.2 | 2.152 | N/A | N/A | N/A | 333.3333 | 3.228 | 750 | 1.4347 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | N/A | #VALUE! | N/A | N/A | Non-Residential | N/A
Medical, Emergency Room | 2.8 | 30.128 | 2.7 | 29.052 | 1.5 | 16.14 | 1.9917 | 21.4309 | 2 | 0.76181 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Exam/Treatment Room | 1.6 | 17.216 | 1.5 | 16.14 | 1.5 | 16.14 | 2.0118 | 21.647 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Nursery | 1 | 10.76 | 0.6 | 6.456 | 1.5 | 16.14 | 1.9917 | 21.4309 | 2 | 0.76181 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Nurse's Station | 1.8 | 19.368 | 1 | 10.76 | 1.5 | 16.14 | 2.0118 | 21.647 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Operating Room | 7.6 | 81.776 | 2.2 | 23.672 | 1.5 | 16.14 | 1.9917 | 21.4309 | 2 | 0.76181 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Patient Room | 1.2 | 12.912 | 0.7 | 7.532 | 1.5 | 16.14 | 1.7218 | 18.5267 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-F Health Occupancy
Medical, Pharmacy | 2.3 | 24.748 | 1.2 | 12.912 | 1.5 | 16.14 | 1.9917 | 21.4309 | 2 | 0.76181 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Radiology/Laboratory | 0.4 | 4.304 | 0.4 | 4.304 | 1.5 | 16.14 | 1.7218 | 18.5267 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Recovery Room | 2.6 | 27.976 | 0.8 | 8.608 | 1.5 | 16.14 | 1.9917 | 21.4309 | 2 | 0.76181 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Medical, Supply Room | 3 | 32.28 | 1.4 | 15.064 | 1.5 | 16.14 | 1.9917 | 21.4309 | 2 | 0.76181 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 160 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Museum, Exhibition Area | 1.6 | 17.216 | 1 | 10.76 | 0.2 | 2.152 | 1.9917 | 21.4309 | 2 | 0.76181 | 1 | 333.3333 | 3.228 | 200 | 5.38 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 3.0119 | 11.4012 | 0.33 | 1.12 | Non-Residential | Table G-F Health Occupancy
Musuem, Restoration Area | 2.5 | 26.9 | 1.7 | 18.292 | 1.5 | 16.14 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 14.9254 | 72.092 | 30 | 35.8667 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.5 |  | 0.5 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Office, Enclosed | 1.5 | 16.14 | 1.1 | 11.836 | 1 | 10.76 | 0.8 | 8.608 | 2 | 0.18581 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.04 | 0.03 | Non-Residential | N/A
Office, Open | 1.3 | 13.988 | 1.1 | 11.836 | 1.5 | 16.14 | 2.5313 | 27.2369 | 2 | 0.7711 | 1 | 100 | 10.76 | 150 | 7.1733 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.04 | 0.06 | Non-Residential | Table G-I Office Occupancy
Parking Garage, Attended | 0.1 | 1.076 | N/A | #VALUE! | 1.5 | 16.14 | 2.5313 | 27.2369 | 2 | 0.7711 | 1 | 100 | 10.76 | 150 | 7.1733 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.15 |  | 0.15 | 120 | 1.004 | 3.8004 | 0.04 | 0.06 | Non-Residential | Table G-I Office Occupancy
Parking Garage, Non-Attended | 0.2 | 2.152 | 0.2 | 2.152 | 0.2 | 2.152 | 0.77995 | 8.3923 | 2 | 0.54813 | 1 | 100 | 10.76 | N/A | #VALUE! | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 0 | 0 | 0 | 0 | Non-Residential | Table G-J Parking Garage Occupancy
Post Office, General | 1.7 | 18.292 | 1.2 | 12.912 | 0.2 | 2.152 | 0.77995 | 8.3923 | 2 | 0.54813 | 1 | 100 | 10.76 | N/A | #VALUE! | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 0 | 0 | 0 | 0 | Non-Residential | Table G-J Parking Garage Occupancy
Religious, Worship | 5.2 | 55.952 | 2.4 | 25.824 | 1 | 10.76 | 1.263 | 13.5902 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0.60766 | 2.3002 | 0 | 0.28 | Non-Residential | Table G-I Office Occupancy
Religious, Worship | 2.3 | 24.748 | 0.9 | 9.684 | 0.5 | 5.38 | 0.41236 | 4.437 | 2 | 0.54813 | 0.4 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 1.53 | Non-Residential | Table G-E Assembly Occupancy
Restrooms | 1 | 10.76 | 0.9 | 9.684 | 0.5 | 5.38 | 0.41236 | 4.437 | 2 | 0.54813 | 0.4 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 1.53 | Non-Residential | Table G-E Assembly Occupancy
Retail, Grocery Store | 2.1* | #VALUE! | 1.7 | 18.292 | 0.2 | 2.152 | 0.8 | 8.608 | N/A | N/A | N/A | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | N/A | #VALUE! | N/A | N/A | Non-Residential | N/A
Retail, Mall Concourse | 1.8 | 19.368 | 1.7 | 18.292 | 1 | 10.76 | 0.90537 | 9.7418 | 2 | 0.47381 | 1 | 30.303 | 35.508 | 60 | 17.9333 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.25 |  | 0.25 | 120 | 5.0198 | 19.002 | 0.35 | 0.05 | Non-Residential | Table G-L Retail Occupancy
Retail, Sales | 2.1* | #VALUE! | 1.7 | 18.292 | 0.5 | 5.38 | 0.5 | 5.38 | N/A | N/A | N/A | 30.303 | 35.508 | 60 | 17.9333 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | 0.25 | 120 | N/A | #VALUE! | N/A | N/A | Retail | Table G-L Retail Occupancy
Sports Arena, Court Sports | 4.3 | 46.268 | 2.3 | 24.748 | 1 | 10.76 | 0.79374 | 8.5407 | 2 | 0.34374 | 1 | 30.303 | 35.508 | 100 | 10.76 | 250 | 73.2188 | 200 | 58.575 | 0.085929 | 0.25 |  | 0.25 | 120 | 0.60766 | 2.3002 | 0.03 | 0.14 | Retail | Table G-L Retail Occupancy
Sports Arena, Indoor Sports Fields | 1.9 | 20.444 | 1.4 | 15.064 | 1 | 10.76 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Sports Arena, Ring Sports | 3.8 | 40.888 | 2.7 | 29.052 | 1 | 10.76 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Stairs, Active | 0.9 | 9.684 | 0.6 | 6.456 | 1 | 10.76 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Stairs, Active | 1.1 | 11.836 | 0.08 | 0.8608 | 0.2 | 2.152 | 0.77995 | 8.3923 | 2 | 0.54813 | 1 | 100 | 10.76 | 100 | 10.76 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.15 |  | 0.15 | 0 | 0 | 0 | 0 | 0 | Non-Residential | N/A
Storage, Active, Musuem | 1.4 | 15.064 | N/A | #VALUE! | 0.2 | 2.152 | 0.27476 | 2.9564 | 2 | 0.18581 | 1 | 333.3333 | 3.228 | 333 | 3.2312 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Storage, Hospital | 2.9 | 31.204 | 0.9 | 9.684 | 0.2 | 2.152 | 0.27476 | 2.9564 | 2 | 0.18581 | 1 | 333.3333 | 3.228 | 333 | 3.2312 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Storage, Inactive, General | 0.3 | 3.228 | 0.3 | 3.228 | 0.2 | 2.152 | 0.27476 | 2.9564 | 2 | 0.18581 | 1 | 333.3333 | 3.228 | 333 | 3.2312 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0 | 0 | 0 | 0 | Non-Residential | Table G-F Health Occupancy
Storage, Inactive, Musuem | 1.4 | 15.064 | 0.8 | 8.608 | 0.2 | 2.152 | 0.27476 | 2.9564 | 2 | 0.18581 | 1 | 333.3333 | 3.228 | 333 | 3.2312 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Storage, Inactive, Musuem | 1.3 | 13.988 | 1.2 | 12.912 | 0.2 | 2.152 | 0.27476 | 2.9564 | 2 | 0.18581 | 1 | 333.3333 | 3.228 | 5000 | 0.2152 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0 | 0 | 0 | 0 | Non-Residential | Table G-N Warehouse Occupancy
Theatre, Performing Arts | 1.8 | 19.368 | 2.6 | 27.976 | 0.5 | 5.38 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transporation, Rail Station/ Bus Terminal | 1 | 10.76 | 0.5 | 5.38 | 0.5 | 5.38 | 1.013 | 10.9002 | 2 | 0.54813 | 1 | 6.993 | 153.868 | 9 | 119.5556 | 245 | 71.7544 | 105 | 30.7519 | 0.045113 | 1.07 |  | 1.07 | 60 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transporation, Rail Station/ Bus Terminal | 0.7 | 7.532 | 0.6 | 6.456 | 0.5 | 5.38 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 30.303 | 35.508 | 60 | 17.9333 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | 0.25 | 120 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transportation, Baggage Area | 1.3 | 13.988 | 1 | 10.76 | 0.5 | 5.38 | 1.1988 | 12.899 | 2 | 0.54813 | 1 | 30.303 | 35.508 | 60 | 17.9333 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | 0.25 | 120 | 0.2642 | 1.0001 | 0.04 | 0.03 | Non-Residential | Table G-E Assembly Occupancy
Transportation, Ticket Counter | 1.8 | 19.368 | 1.5 | 16.14 | 0.5 | 5.38 | 0.5 | 5.38 | N/A | N/A | N/A | 30.303 | 35.508 | 60 | 17.9333 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | 0.25 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-E Assembly Occupancy
Transportation, Ticket Counter | 1.1 | 11.836 | 0.9 | 9.684 | 0.5 | 5.38 | 0.5 | 5.38 | N/A | N/A | N/A | 30.303 | 35.508 | 30 | 35.8667 | 250 | 73.2188 | 250 | 73.2188 | 0.10741 | 0.25 |  | 0.25 | 120 | N/A | #VALUE! | N/A | N/A | Non-Residential | Table G-E Assembly Occupancy
Warehouse, Fine Material | 1.6 | 17.216 | 1.4 | 15.064 | 0.2 | 2.152 | 0.43471 | 4.6775 | 2 | 0.18581 | 1 | 333.3333 | 3.228 | 333 | 3.2312 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0.60766 | 2.3002 | 0 | 0.28 | Non-Residential | Table G-N Warehouse Occupancy
Warehouse, Refrigerated | 1.6 | 17.216 | 1.4 | 15.064 | 0.2 | 2.152 | 0.43471 | 4.6775 | 2 | 0.18581 | 1 | 333.3333 | 3.228 | 333 | 3.2312 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 120 | 0.60766 | 2.3002 | 0 | 0.28 | Non-Residential | Table G-N Warehouse Occupancy
Workshop, General | 2.5 | 26.9 | 1.9 | 20.444 | 0.2 | 2.152 | 0.24282 | 2.6128 | 2 | 0.092903 | 1 | 1000 | 1.076 | 500 | 2.152 | 275 | 80.5406 | 475 | 139.1156 | 0.20408 | 0.15 |  | 0.15 | 0 | 0.60766 | 2.3002 | 0.13 | 0.08 | Non-Residential | Table G-N Warehouse Occupancy

## Conversions
| 1 ft2 | 0.092937 | m2
| 1 m2 | 10.76 | 1 ft2
1 | ft3 / pers | 10.76 | m2/pers
| 1 cubic foot = | 28.3168 | liters
| 1 Btu/h | 0.29287 | W
| 1 kW latent | 1.467 | kg/hr water
| 1 W latent | 0.001467 | kg/hr water
| Enthalpy of evaporation | 2454 | kJ/h/ kg
| Enthalpy of evaporation | 681.6667 | W/ kg

## Notes
Notes
1 | The hot water load for hotels, motels, dormitories, and penetentiaries is 20
gallons/day-occupant for facilities with 20 or fewer rooms; 14 gallong/day-occupant for
facilities with 20 to 100 rooms; and 10 gallons/day-occupant for facilities with more than
100 rooms.
2 | The hot water load for dwellling units shall be calculated as 30 gallons/day per dwelling
unit plus 10 gallons/day per bedroom. Efficiency apartments shall be consdered to have
zero bedrooms.
3 | The hot water load for schools shall be 1.8 gallons/day-occupant for high schools and
0.6 gallons/day-occupant for other schools.
N/A | No default is provided.