## Title
Energy model input data review
Revision: | 00
Date:
Project Name: | S03 Office Tower
Total floors: | Floor NP 4 to NP 20
Gross floor area: | ?
Modeler: | Marcus Jones
North Axis Offset (Degrees): | 40.3
Climate zone:
How to use this sheet: Follow instructions in boxes. Legend below.
Cells with this format are important! They are used to CALCULATE values in the energy model.
Cells with this format are important! They are used DIRECTLY in the model!
Basic project data

## <90.1 Constructions>
Climate zone
Abu Dhabi: 1B
Vienna, Slovakia: 5A
U-Values CZ 5
| Roof type | Roof U | Wall type | Wall U | Floor type | Floor U | Window type | Window U | Window SHGC | Skylight type | Skylight U | Skylight SHGC | Roof albedo
Nonresidential | Insulation entirely above deck | 0.273 | Steel framed | 0.365 | Steel-joist | 0.214 | Metal framing | 2.56 | 0.4 |  | 6.64 | 0.39 | 0.3 | 11.142
Residential | Insulation entirely above deck | 0.273 | Steel framed | 0.365 | Steel-joist | 0.214 | Metal framing | 2.56 | 0.4 |  | 6.64 | 0.39 | 0.3
U-Values CZ 1
| Roof type | Roof U | Wall type | Wall U | Floor type | Floor U | Window type | Window U | Window SHGC | Skylight type | Skylight U | Skylight SHGC | Roof albedo
Nonresidential | Insulation entirely above deck | 0.36 | Steel framed | 0.705 | Steel-joist | 1.986 | Metal framing | 6.81 | 0.25 |  | 11.24 | 0.36 | 0.3
Residential | Insulation entirely above deck | 0.273 | Steel framed | 0.705 | Steel-joist | 1.986 | Metal framing | 6.81 | 0.25 |  | 11.24 | 0.36 | 0.3

## <90.1 Systems
From Table G3.1.1A
Residential building types include dormitory, hotel, motel, and multifamily.
Residential space types include guest rooms, living quarters, private living space, and sleeping quarters. Others space types are non-residential.
| Building Type | Fossil Fuel, Fossil/Electric Hybrid, and Purchased Heat | Electric and Other
1 | Residential | System 1 - PTAC | System 2 - PTHP
2 | Nonres, 3 floors, <2300 m2 | System 3 - PSZ-AC | System 4 - PSZ-HP
3 | Nonres, 4 or 5 floors, <2300 m2 | System 5 - Packaged VAV with Reheat | System 6 - Packaged VAV
| Nonres, >5 floors, 2300 to 14000 m2 | System 5 - Packaged VAV with Reheat | Systm 6 - Packaged VAV
4 | Over 5 floors or > 14000 m2 | System 7 - VAV with Reheat | System 8 - VAV with PFP
| System type | System | Fan | Cooling | Heating
1 | PTAC | Packaged terminal air conditioner | Constant volume | Direct expansion | Hot-water fossil fuel boiler
2 | PTHP | Packaged terminal heat pump | Constant volume | Direct expansion | Electric heat pump
3 | PSZ-AV | Packaged rooftop air conditioner | Constant volume | Direct expansion | Fossil fuel furnace
4 | PSZ-HP | Packaged rootop heat pump | Constant volume | Direct expansion | Electric heat pump
5 | Packaged VAV with Reheat | Packaged rooftop VAV with reheat | VAV | Direct expansion | Hot-water fossil fuel boiler
6 | Packaged VAV with PFP Boxes | Packaged rooftop VAV with reheat | VAV | Direct expansion | Electric resistance
7 | VAV with Reheat | Packaged rooftop VAV with reheat | VAV | Chilled Water | Hot-water fossil fuel boiler
8 | VAV with PFP Boxes | VAV with reheat | VAV | Chilled Water | Electric resistance

## <ASHRAE Space Types>
ASHRAE Space Type Name | Lighting power
W/m2
Office-enclosed | 12
Office-open plan | 12
Conference/ Meeting/ Multipurpose | 14
Classroom/ Lecture/ Training | 15
For Penitentiary | 14
Lobby | 14
For Hotel | 12
For Performing Arts Theater | 36
For Motion Picture Theatre | 12
Audience/ Seating Area | 10
For Gymnasium | 4
For Exercise Center | 3
For Convention Center | 8
For Penitentiary | 8
For Religious Buildings | 18
For Sports Arena | 4
For Performing Arts Theatre | 28
For Motion Picture theatre | 13
For Transportation | 5
Atrium-first three floors | 6
Atrium-each additional floor | 2
Lounge/Recreation | 13
For Hospital | 9
Dining area | 10
For Penitentiary | 14
For Hotel | 14
For Motel | 13
For Bar Lounge/Leisure Dining | 15
For Family Dining | 23
Food Preparation | 13
Laboratory | 15
Restrooms | 10
Dressing/Locker/Fitting Room | 6
Corridor/Transition | 5
For Hospital | 11
For Manufacturing Facility | 5
Stairs – active | 6
Active Storage | 9
For Hospital | 10
Inactive storage | 3
For Museum | 9
Electrical/ mechanical | 16
Workshop | 20
Court Sports Area | 25
Gymnasium/ Exercise Center | 0
Playing Area | 15
Exercise Area | 10
Courthouse/ Police Station/ Penitentiary | 0
Courtroom | 20
Confinement Cells | 10
Judges Chambers | 14
Terminal - Ticket counter | 16
Fire Stations | 0
Fire Station Engine room | 9
Sleeping Quarters | 3
Post Office - Sorting Area | 13
Convention Center - Exhibit Space | 14
Library | 0
Card File & Cataloguing | 12
Stacks | 18
Reading Area | 13
Hospital | 0
Emergency | 29
Recovery | 9
Nurse station | 11
Exam/Treatment | 16
Pharmacy | 13
Patient Room | 8
Operating Room | 24
Nursery | 6
Medical Supply | 15
Physical Therapy | 10
Radiology | 4
Laundry-Washing | 6
Automotive - Service/Repair | 8
Manufacturing | 0
Low Bay | 13
High Bay | 18
Detailed Manufacturing | 23
Equipment room | 13
Control room | 5
Hotel/ Motel Guest Rooms | 12
Dormitory - Living Quarters | 12
Museum | 0
General Exhibition | 11
Restoration | 18
Bank/Office - Banking Activity Area | 16
Religious Buildings | 0
Worship-pulpit | 26
Choir | 10
Fellowship Hall | 10
Retail
Sales area | 18
Mall Concourse | 18
Sports Arena
Ring Sports Area | 29
Indoor Playing Field Area | 15
Warehouse
Fine Material Storage | 15
Medium/Bulky Material Storage | 10
Parking Garage - Garage Area | 2
Transportation
Airport - Concourse | 6
Air/Train/Bus - Baggage Area | 11
For reference: Choose the most similar space type matching the space in the proposed design model, list them in "Spaces" sheet.

## Space Definitions
|  |  | 62.1 | 62.1 | 62.1 | 62.1
|  | Occupancy | Ventilation | Ventilation | Occupancy | Combined | LPD |  | Plug load | Domestic hot water | Heating setpoint |  | Heating setback |  | Cooling Setpoint | Cooling setback
[7 empty] | AD | BL | Same |  | AD | BL | AD | BL | AD | BL
|  | pers/100m | L/s/pers | L/s/m2 | pers/100 m2 | L/s/pers | W/m2 | W/m2 | W/m2 | L/day/pers | C | C | C | C | C | C
Hotel lobby | LOB_HOTEL | 5 | 3.8 | 0.3 | 30 | 4.8 |  | 12 | 5.38 | 0 | 24 | 24 | 18 | 18 | 26 | 30
Storage - Inactive | STORE | 3 | 0 | 0.3 | - | - |  | 3 | 2.15 | 0 | 24 | 24 | 18 | 18 | 26 | 30
Hotel room | ROOM | 7 | 2.5 | 0.3 | 10 | 5.5 |  | 12 | 5.38 | 38 | 24 | 24 | 18 | 18 | 26 | 30
Corridor Transition | CORR | 11 | - | 0.3 | - | - |  | 5 | 5.38 | 0 | 24 | 24 | 18 | 18 | 26 | 30
Dining area / for hotel | DINE_H | 36 | 3.8 | 0.9 | 70 | 5.1 |  | 14 | 5.38 | 38 | 24 | 24 | 18 | 18 | 26 | 30
Retail / Sales area | SALES | 36 | 3.8 | 0.6 | 15 | 7.8 |  | 18 | 5.38 | 0 | 24 | 24 | 18 | 18 | 26 | 30
Retail / Main concourse | CONC | 36 | 3.8 | 0.3 | 40 | 4.6 |  | 18 | 10.76 | 19 | 24 | 24 | 18 | 18 | 26 | 30
Office | OFF | 11 | 2.5 | 0.3 | 5 | 8.5 |  | 12 | 10.76 | 3.8 | 24 | 24 | 18 | 18 | 26 | 30
Office lobby | LOB_OFF |  | 2.5 | 0.3 | 30 | 3.5
Conference/Meeting/Multipurpose | CONF | 72 | 2.5 | 0.3 | 50 | 3.1 |  | 14 | 10.76 | 1 | 24 | 24 | 18 | 18 | 26 | 30
Restrooms | WC | 154 | [5 empty] | 10 | 5.38 | 1 | 24 | 24 | 18 | 18 | 26 | 30
Stairs / Inactive | STAIR | 11 | [5 empty] | 6 | 2.15 | 0 | 24 | 24 | 18 | 18 | 26 | 30
Mechanical rooms | MECH |  | - | 0.3 | - | -

## Schedules
| ASHRAE Space Type | Hourly occupancy fraction
|  | Midnight | [11 empty] | Noon | [7 empty] | Midnight
|  | 00 | 01 | 02 | 03 | 04 | 05 | 06 | 07 | 08 | 09 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23
Hotel lobby
Lighting | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Lighting | Weekend | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Electrical | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Electrical | Weekend | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Occupancy | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Occupancy | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Storage
Lighting | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Lighting | Weekend | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Electrical | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Electrical | Weekend | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Occupancy | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Occupancy | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Room
Lighting | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Lighting | Weekend | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Electrical | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Electrical | Weekend | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Occupancy | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Occupancy | Workday | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Atrium - First three floors | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Atrium - First three floors | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Classroom/Lecture/Training | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Classroom/Lecture/Training | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Conference/Meeting/Multipurpose | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Conference/Meeting/Multipurpose | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Corridor/Transition | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Corridor/Transition | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Court Sports Area | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Court Sports Area | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Dining Area | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Dining Area | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Fellowship Hall | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Fellowship Hall | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Stacks | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Stacks | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Dressing/Locker/Fitting Room | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Electrical/Mechanical | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Electrical/Mechanical | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | NONE | bar: Midnight 00 to Midnight 23
Work | NONE | bar: Midnight 00 to Midnight 23
Weeknd | Office - Enclosed | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Office - Enclosed | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Playing Area | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Playing Area | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Active Storage | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Active Storage | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Weeknd | Restrooms | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%
Work | Restrooms | 0% | 0% | 0% | 0% | 0% | 0% | 10% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 30% | 10% | 10% | 10% | 10% | 10% | 0% | 0% | 0%

## Occupancy
Space Type | Model Code | Floor area | Occupancy | Density | Occupancy | Full-Time Equivalent
|  | m2 | Person, peak | ppl / 100 m2 | m2 / person | FTE Occupants / m2
Office | STOR |  | 50 | 5 | 64
Kitchen (office) | OFFI |  | 300 | 5 | 11.5
Corridor | MECH |  | 50 | 5 | 62
Restrooms | CORR |  | 5000 | 150 | 5.64
Stairs | INAC |  | 50 | 5 | 64
Elec | ATR |  | 1600 | 40 | 2.5
Occupancy Densities have been taken from TABLE 6-1 MINIMUM VENTILATION RATES IN BREATHING ZONE (ASHRAE Standard 62.1-2007), except for Restrooms, Inactive Storgae, Electrical/Mechanical Rooms, Corridor/Transition.
For Atrium, Public Assembly Spaces-Lobbies from the same table is considered.
For each space in the model, estimate occupancy values. (Fill in as much as possible)

## SpacesVentilation
Space Type | Model Code | Design ventilation air | ASHRAE ventilation | ASHRAE ventilation | Served by air system:
|  | L/s/person | L/s/person | L/s/m2 | (Name, type, etc)
Atrium - First three floors | ATRI |  | 2.5 | 0.3
Classroom/Lecture/Training | CLAS |  | 3.8 | 0.3
Conference/Meeting/Multipurpose | CONF |  | 3.8 | 0.3
Corridor/Transition | CORR |  | 2.5 | 0.3
Court Sports Area | COUR |  | 2.5 | 0.6
Dining Area | DINE |  | 3.8 | 0.9
Fellowship Hall | HALL |  | 2.5 | 0.3
Inactive Storage | INAC |  | 2.5 | 0.6
Stacks | LIBR |  | 2.5 | 0.6
Electrical/Mechanical | MECH |  | 2.5 | 0.6
NONE | NONE |  | 3.8 | 0.9
Office - Enclosed | OFFI |  | 2.5 | 0.3
Playing Area | PLAY |  | 5 | 1.5
Active Storage | STOR |  | 2.5 | 0.3
Restrooms | WASH |  | 2.5 | 0.3
For each space in the model, first list appropriate ASHRAE ventilation rate using ASHRAE Std. 62.1. Then, contact client engineer for the actual values for each space type. Estimate as much as possible
Assumptions made for Restrooms, Electrical/ Mechanical Rooms,
Corridor/Transition and Playing area.

## Construction summary
Building Fabric Summary
|  | Baseline Building | Proposed Building |  |  | Input your data here!
| Roof Construction | ASRAE, Insulation entirely above deck; U-0.273 | Architectural design U-0.2 | 0.048079 | 0.035222 | ASRAE, Insulation entirely above deck; U- | 0.273 | Architectural design U- | 0.2
| Above-Grade Wall Construction | Steel framed; U-0.365 | Architectural design U-0.8 | 0.064281 | 0.14089 | Steel framed; U- | 0.365 | Architectural design U- | 0.8
| Below-Grade Wall Construction | Below-grade wall; C-0.365 | Architectural design C-0.365 | 0.064281 | 0.064281 | Below-grade wall; C- | 0.365 | Architectural design C- | 0.365
| Floor/Slab Construction | Slab on grade, F-0.214 | Architectural design F-0.214 | 0.037688 | 0.037688 | Slab on grade, F- | 0.214 | Architectural design F- | 0.214
| Opaque Doors Construction | 0.365 | Architectural design U-0.365 | 0.064281 | 0.064281 |  | 0.365 | Architectural design U- | 0.365
| Vertical Glazing Ratio (gross window-to-wall) | 40% | 80% | 0 | 0
| Vertical Glazing Type and U-value, W/m2K (by orientation) | ASHRAE, U-2.56 | Architectural design U-1.5 | 0.45085 | 0.26417 | ASHRAE, U- | 2.56 | Architectural design U- | 1.5
| Vertical Glazing SHGC (by orientation) | ASHRAE, g-0.4 | Architectural design g-0.32 | 0.070445 | 0.056356 | ASHRAE, g- | 0.4 | Architectural design g- | 0.32
| Vertical Glazing Light Transmittance (by orientation) | N/A | N/A | 0 | 0
| Horizontal Glazing Ratio (gross skylight-to-roof) | 40% | 40% | 0 | 0
| Horizontal Type and U-value, W/m2K | Metal framing; U-6.64 | Architectural design U-1.5 | 1.1694 | 0.26417 | Metal framing; U- | 6.64 | Architectural design U- | 1.5
| Horizontal SHGC | ASHRAE, g-0.39 | Architectural design g-0.32 | 0.068684 | 0.056356 | ASHRAE, g- | 0.39 | Architectural design g- | 0.32
| Horizontal Light Transmittance | N/A | N/A
| Shading Devices | None | Exterior fixed shading
Usi= Uip*5.678263
5.6782
Look up the appropriate U-value for the baseline constructions; roof, walls, and windows. Contact client engineer for proposed values.

## HVAC
HVAC Systems
HVAC System Overview
| Item | Baseline Building | Proposed Building
| Main System Description | 2 water-cooled centrifugal chillers minimum with chillers added so that no chiller is larger than 2813 kW, all sized equally
| Heating System Oversizing | Oversized by 25%
| Cooling System Oversizing | Oversized by 15%
| Hours of Operations: Weekday | 0-24
| Friday | 0-24
| Saturday | 0-24
| Public Holiday | 0-24
Heating System
| Item | Baseline Building | Proposed Building
Heating Generation
Heating Fuel Source
Seasonal Efficiency, kW/kW
Cooling System
| Item | Baseline Building | Proposed Building
| Cooling Generation | Electric heat pump
| Cooling Fuel Source | Electricity
| Seasonal Efficiency, kW/kW | ASHRAE 90.1 tables 6.8.1 Avg. COP-6.1 | Design at ARI 550/590 conditions, COP- | ASHRAE 90.1 tables 6.8.1 Avg. COP- | 6.1 | Design at ARI 550/590 conditions, COP-
| Heat Rejection Type | Water cooled
| Performance & Control | VAV
Design Temperatures, °C
Thermal Zone Set Points
|  | Occupied Hours | Unoccupied Hours
| Cooling Design Temperature | 115 F/ 46.1 C
| Heating Design Temperature | 54 F/12. 2 C
| Temperature Type Modelled | Air
| Max Humidity Set Point | 55%
| Min Humidity Set Point | 45%
HVAC System Pumping
|  | Baseline Building | Proposed Building
Chilled Water Pumps Type & Number
Pump head, m & flow rate, l/s
Pump capacity control
Pump mechanical efficiency, % & power, kW
Condenser Water Pumps Type & Number
Pump head, m & flow rate, l/s
Pump capacity control
Pump mechanical efficiency, % & power, kW
Hot Water Pumps Type & Number
Pump head, m & flow rate, l/s
Pump capacity control
Pump mechanical efficiency, % & power, kW
HVAC System Temperatures
Chilled Water System
|  | Baseline Building | Proposed Building
| Supply Temp, °C | 6.7
| Return Temp, °C | 13
| Reset Temps, °C | N/A
Condenser Water System
|  | Baseline Building | Proposed Building
| Supply Temp, °C | N/A
| Return Temp, °C | N/A
| Reset Temps, °C | N/A
Hot Water System
|  | Baseline Building | Proposed Building
Supply Temp, °C
Return Temp, °C
Reset Temps, °C
Air Side Systems
Baseline Building
Air System Description
| Area Covered, m2 | 82959
Minimum Design Fresh Air Flow, m3/hr
Minimum Design Air Flow (fresh & recirculated), m3/hr
Supply Fan Power, kW & Flow Control
Return Fan Power, kW & Flow Control
Heat Recovery Type
Sensible Effectiveness, %
Latent Effectiveness, %
Proposed Building
Air System Description
Area Covered, m2
Minimum Design Fresh Air Flow, m3/hr
Minimum Design Air Flow (fresh & recirculated), m3/hr
Supply Fan Power, kW & Flow Control
Return Fan Power, kW & Flow Control
Heat Recovery Type
Sensible Effectiveness, %
Latent Effectiveness, %
Capacity kW
Condenser fan capacity
Compressor motor
IMPORTANT: Enter the system COP here.

## Service hot water
Hot water
Service Hot Water System Overview
| System Type | -
| Fuel | -
| Baseline Thermal Efficiency | %
| Proposed Thermal Efficiency | %
| Input Rating | kW
| Tank Capacity | l | 1 kL water per m2
| Tank Insulation R-value | m2.K/W
| Supply Temperature | C
| Demand for abolution, | l/person/day |  | 1.004 | (G/day-occ) | California 2005 ACM
| Demand for Residential | l/bedroom |  | 106 | (Btu/h-occ) | COMNET
| Standby Loss | %/hr
|  |  |  | 3.795 | L/day/occ
| Average Mains Temperature | C
| Average usage temperature | C |  | 31.0655 | W/occ
|  |  |  | 1.3852 | kL/a/occ
Service Hot Water System Pumping
| Number of Pumps |  |  | Hot water: 4 kWh/m2 per annum | http://www.bsria.co.uk/news/poe-stoke/
| Pump Head | m
| Flow Rate | l/s
Control
| Mechanical efficiency | %
| Pump power | kW
Energy use
| Electrical consumption | kWh/a
| Hot water produced | kWh/a

## Process loads
Process load | Process load
kW
Elevators |  | 8 kWh/m2
143104
|  | 65.3443 | 4

## (Variants)
|  | Description | Source File Relative Path | TargetDirectory | Type
Baseline |  | Baseline | C:\Projects2\081_CentralTowerFinal\Project2\IDFupdate\Baseline.idf | . | Baseline
Deletions
|  | This class | With this name
|  | Output:Variable | .
| del | Output:Table:SummaryReports | .
|  | Output:Table:TimeBins | .
| del | OutputControl:Table:Style | .
|  | Boiler:HotWater | .
| del | CoolingTower:SingleSpeed | .
| del | Site:WaterMainsTemperature | .
| del | Output:SQLite | .
Templates
|  | Template ID | Over Zones named … | With this unique name
| tp | Central Elevators
| tp | Central Exhaust Fans
| tp | Summary table output Annual
| tp | Compliance Rotations
Central District Boiler
| tp | Central BL Towers
| tp | Central District Hot Water
| tp | SQL Output
Changes
|  | In this class | With this name | this attribute | becomes
| ch | ^Building$ | . | Name | Baseline
| ch | ^Building$ | . | Solar Distribution | FullExterior
| ch | ^SimulationControl$ | . | Run Simulation for Weather File Run Periods | Yes
| ch | RunPeriod | . | Begin Month | 1
| ch | RunPeriod | . | Begin Day of Month | 1
| ch | RunPeriod | . | End Month | 12
| ch | RunPeriod | . | End Day of Month | 31
| ch | ^Sizing:Zone$ | . | Zone Heating Sizing Factor | 1
| ch | ^Sizing:Zone$ | . | Zone Cooling Sizing Factor | 1
| ch | Exterior:FuelEquipment | Elevators | Design Level | 65000
| ch | Exterior:FuelEquipment | Exhaust Fans | Design Level | 9000
| ch | Branch | Cooling Tower/1 Condenser Loop Branch | Component 1 Object Type | CoolingTower:TwoSpeed
| ch | Branch | Cooling Tower Condenser Loop Branch | Component 1 Object Type | CoolingTower:TwoSpeed
|  | Branch | District Heating Connection HW Plant Loop Branch | Component 1 Object Type | DistrictHeating
|  | PlantEquipmentList | ^HW Loop Scheme 1 Range 1 Equipment List | Equipment 1 Object Type | DistrictHeating
| ch | PlantEquipmentList | ^Condenser Loop CH1 Scheme 1 Range 1 Equipment List | Equipment 1 Object Type | CoolingTower:TwoSpeed
| ch | PlantEquipmentList | ^Condenser Loop CH2 Scheme 1 Range 1 Equipment List | Equipment 1 Object Type | CoolingTower:TwoSpeed
|  | Fan:VariableVolume | AHU Bottem 4-12 AHU Extract Fan | Pressure Rise | 904.3272
|  | Fan:VariableVolume | AHU Bottem 4-12 AHU Supply Fan | Pressure Rise | 904.3272
|  | Fan:VariableVolume | AHU 8NP AHU Extract Fan | Pressure Rise | 944.1084
|  | Fan:VariableVolume | AHU 8NP AHU Supply Fan | Pressure Rise | 944.1084
|  | Fan:VariableVolume | AHU 20NP AHU Extract Fan | Pressure Rise | 944.1025
|  | Fan:VariableVolume | AHU 20NP AHU Supply Fan | Pressure Rise | 944.1025
|  | Fan:VariableVolume | AHU Top 13-19 AHU Extract Fan | Pressure Rise | 904.32
|  | Fan:VariableVolume | AHU Top 13-19 AHU Supply Fan | Pressure Rise | 904.32
|  | Fan:VariableVolume | AHU Bottem 4-12 AHU Extract Fan | Motor Efficiency | 0.95
|  | Fan:VariableVolume | AHU Bottem 4-12 AHU Supply Fan | Motor Efficiency | 0.95
|  | Fan:VariableVolume | AHU 8NP AHU Extract Fan | Motor Efficiency | 0.91
|  | Fan:VariableVolume | AHU 8NP AHU Supply Fan | Motor Efficiency | 0.91
|  | Fan:VariableVolume | AHU 20NP AHU Extract Fan | Motor Efficiency | 0.91
|  | Fan:VariableVolume | AHU 20NP AHU Supply Fan | Motor Efficiency | 0.91
|  | Fan:VariableVolume | AHU Top 13-19 AHU Extract Fan | Motor Efficiency | 0.95
|  | Fan:VariableVolume | AHU Top 13-19 AHU Supply Fan | Motor Efficiency | 0.95
|  | Pump:VariableSpeed | HW Loop Supply Pump/1 | Rated Flow Rate | 0.0215
|  | Pump:VariableSpeed | HW Loop Supply Pump/1 | Rated Pump Head | 50000
|  | Pump:VariableSpeed | HW Loop Supply Pump/1 | Rated Power Consumption | 6475
|  | Pump:VariableSpeed | CHW Loop Supply Pump/1 | Rated Flow Rate | 0.077
|  | Pump:VariableSpeed | CHW Loop Supply Pump/1 | Rated Pump Head | 50000
|  | Pump:VariableSpeed | CHW Loop Supply Pump/1 | Rated Power Consumption | 26853.288
|  | Pump:VariableSpeed | DHW Pump | Rated Flow Rate | 0.002
|  | Pump:VariableSpeed | DHW Pump | Rated Pump Head | 50000
|  | Pump:VariableSpeed | DHW Pump | Rated Power Consumption | 500
|  | Pump:ConstantSpeed | Condenser Loop CH1 Supply Pump | Rated Flow Rate | 0.061
|  | Pump:ConstantSpeed | Condenser Loop CH1 Supply Pump | Rated Pump Head | 50000
|  | Pump:ConstantSpeed | Condenser Loop CH1 Supply Pump | Rated Power Consumption | 18372.468
|  | Pump:ConstantSpeed | Condenser Loop CH2 Supply Pump | Rated Flow Rate | 0.061
|  | Pump:ConstantSpeed | Condenser Loop CH2 Supply Pump | Rated Pump Head | 50000
|  | Pump:ConstantSpeed | Condenser Loop CH2 Supply Pump | Rated Power Consumption | 18372.468
As Designed |  | As Designed | C:\Projects2\081_CentralTowerFinal\Project2\IDFupdate\As Designed.idf | . | Proposed
Deletions
|  | This class | With this name
|  | Output:Variable | .
| del | Output:Table:SummaryReports | .
|  | Output:Table:TimeBins | .
| del | OutputControl:Table:Style | .
|  | Boiler:HotWater | .
| del | Site:WaterMainsTemperature | .
| del | Output:SQLite | .
Templates
|  | Template ID | Over Zones named … | With this unique name
| tp | Central Elevators
| tp | Central Exhaust Fans
| tp | Summary table output Annual
Central District Boiler
| tp | Central District Hot Water
SQL Output
Changes
|  | In this class | With this name | this attribute | becomes
| ch | ^Building$ | . | Name | As Designed
| ch | ^Building$ | . | Solar Distribution | FullExterior
| ch | ^SimulationControl$ | . | Run Simulation for Weather File Run Periods | Yes
| ch | RunPeriod | . | Begin Month | 1
| ch | RunPeriod | . | Begin Day of Month | 1
| ch | RunPeriod | . | End Month | 12
| ch | RunPeriod | . | End Day of Month | 31
| ch | ^Sizing:Zone$ | . | Zone Heating Sizing Factor | 1
| ch | ^Sizing:Zone$ | . | Zone Cooling Sizing Factor | 1
|  | Branch | District Heating Connection HW Plant Loop Branch | Component 1 Object Type | DistrictHeating
|  | PlantEquipmentList | HW Loop Scheme 1 Range 1 Equipment List | Equipment 1 Object Type | DistrictHeating
| ch | Exterior:FuelEquipment | Elevators | Design Level | 65000
| ch | Exterior:FuelEquipment | Exhaust Fans | Design Level | 9000
|  | Pump:VariableSpeed | HW Loop Supply Pump/1 | Rated Flow Rate | 0.0063611
|  | Pump:VariableSpeed | HW Loop Supply Pump/1 | Rated Pump Head | 50000
|  | Pump:VariableSpeed | HW Loop Supply Pump/1 | Rated Power Consumption | 790
|  | Pump:VariableSpeed | DHW Pump | Rated Flow Rate | 0.002
|  | Pump:VariableSpeed | DHW Pump | Rated Pump Head | 50000
|  | Pump:VariableSpeed | DHW Pump | Rated Power Consumption | 500
|  | Fan:ConstantVolume | Bottom DOAS VAV AHU Extract Fan | Pressure Rise | 540
|  | Fan:ConstantVolume | Bottom DOAS VAV AHU Supply Fan | Pressure Rise | 540
|  | Fan:ConstantVolume | Top DOAS VAV AHU Extract Fan | Pressure Rise | 540
|  | Fan:ConstantVolume | Top DOAS VAV AHU Supply Fan | Pressure Rise | 540
|  | Fan:ConstantVolume | Top DOAS VAV AHU Supply Fan | Maximum Flow Rate | 9.7222
|  | Fan:ConstantVolume | Bottom DOAS VAV AHU Extract Fan | Maximum Flow Rate | 9.7222
|  | Fan:ConstantVolume | Bottom DOAS VAV AHU Supply Fan | Maximum Flow Rate | 9.7222
|  | Fan:ConstantVolume | Top DOAS VAV AHU Extract Fan | Maximum Flow Rate | 9.7222
END
Don't edit this!
Don't edit this!
Don't edit this!

## (GlobalSettings)
Run control
Project:
Structure revision:
Created by | Marcus Jones
Date:
Set global parameters here
| This root directory | C:\Projects2\081_CentralTowerFinal\Project2\IDFupdate\
| Baseline model file | C:\Projects2\081_CentralTowerFinal\Project2\IDFupdate\Baseline.idf |  | Baseline.idf
| Design model file | C:\Projects2\081_CentralTowerFinal\Project2\IDFupdate\As Designed.idf |  | As Designed.idf
^SimulationControl$ | Weather File Run Periods | Yes
^Building$ | Solar Distribution | FullExterior
RunPeriod | Begin Month | 1
RunPeriod | End Month | 12
^Building$ | Solar Distribution | FullExterior
^Building$ | 0 North Axis | 40.3
^Building$ | 90 North Axis | 130.3
^Building$ | 180 North Axis | 220.3
^Building$ | 270 North Axis | 310.3
Baseline vs. Proposed
| Baseline | Proposed | Other?
Walls Massless R | 1.9997 | 0.51 |  |  |  |  | Air Change
Roof Massless R | 2.933 | 4.27 |  |  | #N/A |  | Baseline
Floor Massless R | 6 | 6 |  |  |  |  | #N/A
Window U | 2.56 | 1.5 |  |  |  |  | 1
Window SHGC | 0.4 | 0.32 |  |  |  |  | #N/A
Air Changes per Hour | 0.3 | 0.3
Lighting W/m2 | #REF! | #REF!
Nominal COP | 0 | 0
Heating size | 1.25 | 1
Cooling size | 1.15 | 1
Plug Load | #REF! | #REF!
Occupancy | 0.07 | 0.07
U - Values worksheet
|  |  | Target |  | Film | Remainder | Massive layer |  |  | Massles layer
|  |  | U | R | R | R | t | k | R | R
|  |  | W/m2.K | m2.K/W | m2.k/W | m2.K/W | m | W/k.m2 | m2.K/W | m2.K/W
Baseline |  | Walls | 0.365 | 2.7397 | 0.14 | 2.5997 | 0.3 | 0.5 | 0.6 | 1.9997
|  | Roof | 0.273 | 3.663 | 0.13 | 3.533 | 0.3 | 0.5 | 0.6 | 2.933
|  | Floor | 1.264 | 0.79114 |  | 0.79114 | 0.3 | 0.5 | 0.6 | 0.19114
Design |  | Walls | 0.8 | 1.25 | 0.14 | 1.11 | 0.3 | 0.5 | 0.6 | 0.51
|  | Roof | 0.2 | 5 | 0.13 | 4.87 | 0.3 | 0.5 | 0.6 | 4.27
|  | Floor | 1.264 | 0.79114 |  | 0.79114 | 0.3 | 0.5 | 0.6 | 0.19114
COP Worksheet
SCOP
Nominal COP
Hot water
|  | m3/s | U: Frac
| Shower peak flow | 0.000175 | U: 0.1
| Sink peak flow | 0.001575 | U: 0.9
| Average outdoor temp | 13 | bar: U
| Max monthly diff | 19 | bar: U
|  | Num Pers | U: 700; R: pers
|  | Peak office rate | U: 9; R: L/hr/pers
|  | Peak office rate | U: 2.5e-06; R: m3/hr/pers
|  | Total peak rate | U: 0.00175; R: m3/hr

## Spaces OLD
Space Type | ASHRAE Space | Model Code | Area | Unique | Model Code | TOTAL BUILDING
4NP |  |  | m2
Offices | Office-open plan | OFFI | 735.9
Stairs | Stairs – active | STAIR | 23 |  |  |  | Total over all floors
Kitchen | Food Preparation | KITCH | 5.3 |  | Offices, conference, kitchen, washrooms | 870 | 14790 | 158400.9
Cleaning | Active Storage | CLNG | 3 |  | Ancilliary | 121 | 2057 | 22030.47
Washrooms | Restrooms | WASH | 23 |  | Corridors and stairs | 61 | 1037 | 11106.27
Storage | Active Storage | STOR | 8
Corridor | Corridor/Transition | CORR | 20.3 |  |  | Grand total | 17884 | m2
Mechanical | Electrical/ mechanical | MECH | 79.4 |  |  |  | 191537.64 | sf
(Void space, shafts) |  | VOID | 63.1 |  |  | TARGET | 191650 | sf
|  | TOTAL GFA AREA | 961
5NP-19NP
Offices | Office-open plan | OFFI | 815.3
Stairs | Stairs – active | STAIR | 23
Kitchen | Food Preparation | KITCH | 5.3
Cleaning | Active Storage | CLNG | 3
Washrooms | Restrooms | WASH | 23
Storage | Active Storage | STOR | 8
Corridor | Corridor/Transition | CORR | 20.3
(Void space, shafts) |  | VOID | 63.1
|  | TOTAL GFA AREA | 961
20NP
Offices | Office-open plan | OFFI | 660.9
Stairs | Stairs – active | STAIR | 23
Kitchen | Food Preparation | KITCH | 5.3
Cleaning | Active Storage | CLNG | 3
| Restrooms | WASH | 23
| Active Storage | STOR | 8
| Corridor/Transition | CORR | 20.3
Mechanical | Electrical/ mechanical | MECH | 128.5
(Void space, shafts) |  | VOID | 89
|  | TOTAL GFA AREA | 961
21NP
(Unconditioned)
Total
|  |  | 16337 | m2
175849.8343
Roof Floor
Social Activity Club | Conference/Meeting/Multipurpose | CONF
Corridor | Corridor/Transition | CORR
Lift's Room | Electrical/Mechanical | MECH
Mechanical Room | Electrical/Mechanical | MECH
Column: | Column:
20 | 21